## SSO SUMMARY
The first two sections count the number of events and volume amounts for each type of Sanitary Sewer Overflow (SSO) for each municipality and in total | [30 empty] | This secion keeps track of the approximate gallons spilled from SSOs by municipality - a combined total of CSOs and SSOs is on the Reached Water Summary Tab
Municipality | # of SSO Events | # of NPDES Permitted Bypasses | # ot TOTAL EVENTS | All Events Total Estimated Gallons | # Reached Water |  | # Excessive Flows - Storm Event | Volume (gallons) Excessive Flows - Storm Event | # Excessive Flows - Snow Melt | Volume (gallons) Excessive Flows - Snow Melt | # Electrical Equipment Failure | Volume (gallons) Eletrical Equipt Failure | # Mechanical Equipment Failure | Volume (gallons) Mech Equipt Failure | # Other - Sewer Break, Crack or Failure | Volume (gallons) Other - Sewer Break, Crack or Failure | # Other - Contractor or Operator Error or other mechanical | Volume (gallons) Other - Contractoror Operator error or other mechanical | # Sewer Line Blockage - Grease | Volume (gallons) Line Blockage - Grease | # Sewer Line Blockage - Rags | Volume (gallons) Line Blockage - Rags | # Sewer Line Blockage - Roots | Volume (gallons) Line Blockage - Roots | # Sewer Line Blockage - Debris (Bricks, Carts,Silt, etc) | Volume (gallons) Link Bolckage - Debris (Bricks, Carts, Silt, etc) | # Sewer Line Blockage - Other | Volume (gallons) Link Bolckage - Other | # Unknown Cause | Volume (gallons) Unknown Cause | Unnamed Waterbody (gallons) | 5 Mile River (gallons) | Ash Creek (gallons) | Avery Brook (gallons) | Bantam River (gallons) | Beaver Brook (gallons) | Black Rock Harbor / LIS (gallons) | Bride Brook (gallons) | Bridgeport Harbor / LIS (gallons) | Bristol Fish & Game Club Pond (gallons) | Bruce Brook (gallons) | Cedar Creek / LIS (gallons) | Connecticut River (gallons) | Copper Mine Brook (gallons) | Deckers Brook (gallons) | Farmington River (gallons) | Goodwives River (gallons) | Greenwich Cove / Harbor (gallons0 | Hockanum River (gallons) | Holly Pond (gallons) | Housatonic River (gallons) | Indian River (gallons) | Keeler Brook (gallons) | Little River (gallons) | Long Island Sound (gallons) | Long Meadow Pond Brook (gallons) | Mad River (gallons) | Mattabassett River (gallons) | Middle Pond (gallons) | Mill Brook (gallons) | Mill Pond (gallons) | Mill River (gallons) | Moosup River (gallons) | Muddy Brook (gallons) | Naugatuck River (gallons) | New Haven Harbor (gallons) | Old Field Creek (gallons) | Park River (incl N, S & Conduit) (gallons) | Piper Brook (gallons) | Pomperug River (gallons) | Quinnipiac River (gallons) | Rooster River (gallons) | Saugatuck River (gallons) | Seeley Pond (gallons) | Shetucket River (gallons) | Stamford Harbor East Branch (gallons) (gallons) | Steele Brook (gallons) | Still River (gallons) | Stony Brook River (gallons) | Thames River (gallons) | Thurston Pnd (gallons) | Trout Brook (gallons) | Trumpet Brook (gallons) | Webster Brook (gallons) | Welton Brook (gallons) | Wilson Cove (gallons)
Beacon Falls | 2 | 0 | 2 | 9800 | 2 |  | 2 | 9800 | [56 empty] | 9800
Berlin | 3 | 0 | 3 | 1600 | 0 |  | 1 | 800 | [10 empty] | 2 | 800
Bloomfield | 2 | 0 | 2 | 859 | 0 | [11 empty] | 1 | 850 | 1 | 9
Branford | 2 | 0 | 2 | 350 | 0 | [13 empty] | 1 | 300 | 1 | 50
Bridgeport | 16 | 35 | 51 | 176700052 | 40 |  | 35 | 176697222 | [10 empty] | 9 | 1530 | 7 | 1300 | [14 empty] | 580 |  | 45130000 |  | 150 | 116597222 | [12 empty] | 14970300 | [16 empty] | 100 |  | 200
Bristol | 8 | 0 | 8 | 146013 | 2 |  | 2 | 61500 | [10 empty] | 2 | 98 | 2 | 115 |  |  | 2 | 84300 | [13 empty] | 30000 |  |  |  | 31500
Cheshire | 2 | 0 | 2 | 2003000 | 1 |  | 1 | 3000 | [6 empty] | 1 | 2000000 | [45 empty] | 2000000
Coventry | 3 | 0 | 3 | 58000 | 0 |  | 1 | 21000 | [8 empty] | 2 | 37000
Cromwell | 10 | 0 | 10 | 71401548 | 10 |  | 10 | 71401548 | [34 empty] | 71329548 | [14 empty] | 72000
Danbury | 4 | 0 | 4 | 7918850 | 4 |  | 2 | 7918000 | [10 empty] | 1 | 500 | 1 | 350
Darien | 3 | 0 | 3 | 346 | 2 |  | 2 | 346 | [6 empty] | 1 | 0 | [30 empty] | 346
Derby | 3 | 0 | 3 | 110090 | 2 |  | 1 | 70000 |  |  |  |  | 1 | 40000 | 1 | 90 | [34 empty] | 110000
East Haddam | 1 | 0 | 1 | 10000 | 1 | [9 empty] | 1 | 10000 | [26 empty] | 10000
East Hartford | 3 | 0 | 3 | 95 | 0 | [13 empty] | 1 | 85 | [6 empty] | 1 | 1 | 1 | 9
East Haven | 1 | 0 | 1 | 5 | 0 | [9 empty] | 1 | 5
East Lyme | 1 | 0 | 1 | 31200 | 1 | [9 empty] | 1 | 31200 | [21 empty] | 31200
Fairfield | 17 | 0 | 17 | 77355 | 1 |  | 10 | 75000 |  |  |  |  | 1 | 1500 |  |  |  |  | 2 | 275 | 2 | 475 | 2 | 105 | [8 empty] | 11000
Glastonbury | 1 | 0 | 1 | 240 | 0 | [13 empty] | 1 | 240
Granby | 1 | 0 | 1 | 50 | 0 | [7 empty] | 1 | 50
Greenwich | 3 | 0 | 3 | 61300 | 3 |  | 1 | 200 | [6 empty] | 1 | 100 | 1 | 61000 | [12 empty] | 100 | [16 empty] | 61200
Groton | 11 | 0 | 11 | 1550 | 1 | [5 empty] | 1 | 630 |  |  | 1 | 25 | 1 | 300 | 2 | 10 |  |  | 1 | 90 | 2 | 360 |  |  | 3 | 135 | [49 empty] | 630
Hartford | 18 | 0 | 18 | 184599 | 4 |  | 6 | 1300 | [6 empty] | 2 | 20 | 3 | 180000 | 3 | 189 | [8 empty] | 4 | 3090 | [37 empty] | 180090
Litchfield | 2 | 0 | 2 | 79300 | 1 | [15 empty] | 1 | 43300 | 1 | 36000 | [10 empty] | 36000
Manchester | 3 | 0 | 3 | 201590 | 1 | [13 empty] | 2 | 201500 |  |  | 1 | 90 | [24 empty] | 200000
Mansfield | 2 | 0 | 2 | 75900 | 0 |  |  |  | 1 | 75000 |  |  |  |  | 1 | 900
Meriden | 2 | 0 | 2 | 540750 | 1 |  | 1 | 540000 | [10 empty] | 1 | 750 | [50 empty] | 540000
Middletown | 1 | 0 | 1 | 90 | 0 | [17 empty] | 1 | 90
Milford | 5 | 0 | 5 | 13600365 | 3 |  | 2 | 13600000 |  |  |  |  | 2 | 280 |  |  | 1 | 85 | [12 empty] | 80 | [19 empty] | 13600000
Montville | 6 | 0 | 6 | 5004000 | 4 |  | 3 | 5000000 | [6 empty] | 3 | 4000 | [63 empty] | 5001000
Naugatuck | 6 | 0 | 6 | 198675 | 4 |  | 2 | 195000 | [6 empty] | 1 | 200 | 1 | 1800 | 1 | 175 |  |  | 1 | 1500 | [31 empty] | 1800 | [8 empty] | 195000 | [15 empty] | 1500
New Canaan | 1 | 0 | 1 | 367000 | 1 | 1 | 1 | 367000 | [23 empty] | 367000
New Haven | 9 | 64 | 73 | 305829220 | 66 |  | 66 | 305827600 |  |  |  |  | 1 | 45 | 1 | 45 | 1 | 450 | 2 | 130 |  |  |  |  | 2 | 950 | [39 empty] | 305827600
New London | 3 | 0 | 3 | 155000 | 3 |  | 2 | 6000 | [8 empty] | 1 | 149000 | [61 empty] | 155000
Newington | 8 | 0 | 8 | 1552700 | 6 |  | 8 | 1552700 | [51 empty] | 20850 | [23 empty] | 1531670
North Haven | 3 | 0 | 3 | 803 | 0 | [9 empty] | 1 | 40 | [6 empty] | 1 | 13 |  |  |  |  | 1 | 750
Norwalk | 10 | 0 | 10 | 1739782 | 5 |  | 1 | 1700000 |  |  |  |  | 4 | 37562 | 3 | 1690 | 1 | 450 |  |  | 1 | 80 | [29 empty] | 34362 | 1700450 | [19 empty] | 800 | [12 empty] | 2500
Norwich | 9 | 0 | 9 | 5074010 | 6 |  | 1 | 100 |  |  |  |  | 2 | 213224 | 2 | 887387 |  |  | 1 | 10000 | 2 | 43429 |  |  | 1 | 3919870 | [48 empty] | 263653 |  |  |  |  | 4804757
Orange | 1 | 0 | 1 | 20 | 0 | [11 empty] | 1 | 20
Oxford | 1 | 0 | 1 | 40000 | 1 | [9 empty] | 1 | 40000 | [37 empty] | 40000
Plainfield | 3 | 0 | 3 | 1750 | 2 | [5 empty] | 1 | 1000 | 1 | 300 |  |  | 1 | 450 | [44 empty] | 1300
Plymouth | 5 | 0 | 5 | 2725 | 1 | [9 empty] | 3 | 1625 |  |  | 1 | 1000 |  |  |  |  | 1 | 100 | [32 empty] | 1000
Ridgefield | 1 | 0 | 1 | 70 | 0 | [13 empty] | 1 | 70
Seymour | 1 | 0 | 1 | 20475 | 1 |  | 1 | 20475 | [56 empty] | 20475
Shelton | 4 | 0 | 4 | 263 | 0 | [9 empty] | 1 | 200 |  |  |  |  | 1 | 45 | [6 empty] | 2 | 18
Simsbury | 2 | 0 | 2 | 4980015 | 2 |  | 1 | 4980000 | [12 empty] | 1 | 15 | [23 empty] | 4980015
South Windsor | 4 | 0 | 4 | 24190 | 3 | [5 empty] | 2 | 20100 |  |  |  |  | 1 | 4000 |  |  | 1 | 90 | [11 empty] | 90 | [8 empty] | 20100
Southbury | 4 | 0 | 4 | 28110 | 2 | [9 empty] | 3 | 28100 | [6 empty] | 1 | 10 | [45 empty] | 28000
Southington | 4 | 0 | 4 | 7497530 | 2 |  | 2 | 7497000 |  |  | 1 | 500 | [16 empty] | 1 | 30 | [40 empty] | 7497000
Stamford | 6 | 0 | 6 | 159020 | 5 |  | 3 | 151020 |  |  |  |  | 1 | 1000 | 1 | 3000 | 1 | 4000 | [31 empty] | 20 | [25 empty] | 155000
Stratford | 7 | 0 | 7 | 37000180 | 6 |  | 4 | 33700000 | [6 empty] | 1 | 3300000 | 1 | 90 | [6 empty] | 1 | 90 | [24 empty] | 37000090
Torrington | 4 | 0 | 4 | 570 | 3 | [7 empty] | 1 | 10 | 1 | 50 |  |  | 1 | 500 | 1 | 10 | [8 empty] | 500 | [46 empty] | 60
Trumbull | 5 | 0 | 5 | 17100 | 0 | [9 empty] | 3 | 15300 | 1 | 300 |  |  |  |  | 1 | 1500
Vernon | 2 | 0 | 2 | 1025 | 2 | [7 empty] | 1 | 50 | 1 | 975 | [32 empty] | 1025
Waterbury | 14 | 0 | 14 | 1206063 | 11 |  | 6 | 1121403 |  |  |  |  | 1 | 180 | 3 | 78600 |  |  |  |  | 1 | 3750 |  |  |  |  | 3 | 2130 | [7 empty] | 100 | [20 empty] | 3750 | [7 empty] | 846153 | [11 empty] | 5400 | [5 empty] | 73200 |  | 275250
West Hartford | 36 | 0 | 36 | 179142200 | 32 |  | 32 | 179141800 | [10 empty] | 1 | 100 |  |  | 1 | 100 | 1 | 100 |  |  | 1 | 100 | [38 empty] | 129015850 | [12 empty] | 50125950
West Haven | 6 | 0 | 6 | 4020870 | 4 |  | 5 | 4020820 | [12 empty] | 1 | 50 | [32 empty] | 2000 | [11 empty] | 401350
Westport | 3 | 0 | 3 | 153150 | 3 |  | 1 | 3000 | [6 empty] | 1 | 150000 | 1 | 150 | [42 empty] | 150 |  |  | 150000 | [14 empty] | 3000
Wethersfield | 8 | 0 | 8 | 1200 | 2 |  | 6 | 600 | [16 empty] | 1 | 500 |  |  | 1 | 100 | [5 empty] | 200
Windsor | 10 | 0 | 10 | 32550 | 2 |  | 9 | 32450 | [20 empty] | 1 | 100 | [14 empty] | 850 | 30000
Winsted | 1 | 0 | 1 | 10000 | 0 | [11 empty] | 1 | 10000
SUMMARY | 317 | 99 | 416 | 827475163 | 259 |  | 231 | 815716684 | 1 | 75000 | 5 | 22230 | 17 | 294201 | 41 | 6553552 | 21 | 449945 | 36 | 218261 | 23 | 93059 | 11 | 39498 | 11 | 4006270 | 4 | 2131 | 15 | 4332 | 680 | 367000 | 11000 | 90 | 36000 | 300 | 580 | 31200 | 45130000 | 30000 | 150 | 116597222 | 71359648 | 31500 | 850 | 5010015 | 346 | 61200 | 201025 | 20 | 50710090 | 34362 | 1700450 | 40000 | 14972300 | 1800 | 3750 | 72000 | 1000 | 20850 | 150 | 2000000 | 1300 | 150000 | 1071428 | 305827600 | 401350 | 180090 | 129015850 | 28000 | 8037000 | 100 | 800 | 200 | 263653 | 155000 | 5400 | 60 | 3000 | 9961387 | 1500 | 50125950 | 73200 | 1531670 | 275250 | 2500
[8 empty] | Event Count | 416
[8 empty] | Gallons Count | 827475163
[31 empty] | TOTAL REACHED WATER: |  |  |  | 815537866
Data Caveats
While DEEP is the storehouse for the SRTK data, DEEP makes the following caveats:
· All data is submitted by publicly owned wastewater treatment plants and publicly owned satellite collection systems.
· DEEP does not issue notifications about individual discharges, they are inputted by the reporters for each municipality and issued by the electronic system automatically.
· The reports are being submitted by the municipalities in a short time frame after discovery of a discharge and specific details may not be known.
· Data is estimated based on the existing systems, models, and personal knowledge of the sewer systems by the reporters.
· Data quality, especially volumes, is not checked by DEEP.
· The electronic program allows for zero duration, short durations and zero quantities for volumes.
· Addresses may not be entered by municipalities in a way that allows the parts of the address to be separated nor with an exact location.
· Multiple notifications may be sent for the same discharge since municipalities need to submit daily and termination reports for ongoing discharges.
· Duplicate reports and reports submitted that resulted in zero flow may be rescinded in the system.

## BEACON FALLS
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BEACON FALLS | Closed | Sewage Bypass | Dry | 2024-05-31 | 07:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | unbalanced secondaries | solids in our effluent | 8800 gallons | estimate off prior days flow chart | Yes | Naugatuck River | 2024-05-31 | 08:00 AM | 8800 gallons | 8800 |  | Balanced secondaries | Beacon Falls | 411 Lopus Rd, Beacon Falls, CT
BEACON FALLS | Closed | Sewage Bypass | Dry | 2024-03-08 | 00:00 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | excessive flows | When we arrive at 7;00am solids were leaving our secondaries. | unsure |  | Yes | Naugatuck river | 2024-03-08 | 07:30 AM | unsure | 1000 |  | balanced the secondaries | Beacon Falls | 411 Lopus Rd, Beacon Falls, CT
[17 empty] | TOTAL VOLUME | 9800

## BERLIN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-02-28 | 07:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Sewer leaking from manhole | 500 gph | estimated | No |  | 2024-02-28 | 08:30 AM | 500 | 500 |  |  | Berlin | 847 Farmington Ave, Berlin, CT
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-02-28 | 05:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Sewage was seen coming from manhole | 100 gph | Visual observation | No |  | 2024-02-28 | 07:00 AM | 300 gallons | 300 |  | Sewer main was jetted. | Berlin | 848 Farmington Ave, Berlin, CT
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-01-10 | 06:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Morning rounds | 100 gallons / hour | estimated | No |  | 2024-01-10 | 02:00 PM | 800 gallons | 800 |  | storm ended | Berlin | 34 Upson Ave, Berlin, CT
[17 empty] | TOTAL VOLUME | 1600

## BLOOMFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-10-03 | 09:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | CUSTOMER CALL | LESS THAN 10 GAL | MDC PERSONNEL | No |  | 2024-10-04 | 04:30 AM | LESS THAN 10 GAL. | 9 |  | JET TRUCK RELIEVED BLOCKAGE. | Bloomfield | 10 Wintonbury Ave, Bloomfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-04-24 | 03:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | CONTRACTOR WHILE RELINING SEWER MAIN | MDC SUPERVISOR | < 1000 | MDC SUPERVISOR | No |  | 2024-04-24 | 07:00 PM | 100-1000g | 850 |  | Contractor resolved issue - hired cleaning company - Event has ended | Bloomfield | 44 Burnwood Dr, Bloomfield, CT
[17 empty] | TOTAL VOLUME | 859

## BRANFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRANFORD | Closed | Sewage Bypass | Dry | 2024-02-06 | 07:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | the sewer line was backed up due to a build up of rags. | police called sewer department stand by person | 50 gallons | visual | No |  | 2024-02-06 | 07:45 PM | 50 gallons | 50 |  | the sewer line was jetted | Branford | 68 Elm St, Branford, CT
BRANFORD | Closed | Sewage Bypass | Dry | 2024-01-08 | 04:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | build up of grease. | Police department notified sand by sewer personal | 300 gallons | visual | No |  | 2024-01-08 | 05:00 AM | 300 gallons | 300 |  |  | Branford | 112 N Main St, Branford, CT
[17 empty] | TOTAL VOLUME | 350

## BRIDGEPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-12-31 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observations | N/A | N/A | Yes | Long Island sound | 2025-01-01 | 02:30 AM | 1.41 mg | 1410000 |  | event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-12-17 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | resident called | 150 gals | estimated visual | Yes | Bruce Brook | 2024-12-17 | 11:45 AM' | 150gals | 150 |  | High pressure jet clear main line | Bridgeport | 1905 Barnum Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-12-11 | 07:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | N/A | Visual Observation | N/A | N/A | Yes | Long Island Sound | 2024-12-11 | 09:30 AM | 0.81 mg | 810000 |  | event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-12-09 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | resident call in | Unknown | NA | No | NA | 2024-12-09 | 11:45 AM' | Unknown | 100 |  | high pressure jet surcharged main line | Bridgeport | 56 Durando Pl, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-12-02 | 12:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | resident called in | Unknown | NA | No |  | 2024-12-02 | 01:15 PM | Unknown | 100 |  | High pressure clean surcharged main line | Bridgeport | 975 Lakeside Dr, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-11-19 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | homeowner called | Unknown | NA | No |  | 2024-11-19 | 01:30 PM | Unknown | 100 |  | cleaned surcharged main line | Bridgeport | 262 Bronx Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-11-12 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Homeowner called in | NA | NA | No |  | 2024-11-12 | 10:45 AM | NA | 100 |  | Jetted main line with high pressure hose | Bridgeport | 336 Benham Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-10-21 | 03:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags, main line surcharged | Homeowner called | Unknown | Cleaned main line using high pressure Jet/vac | No |  | 2024-10-21 | 04:15 PM | NA | 100 |  | cleared main line surcharge with high pressure Jet/vac, ball of rags and grease | Bridgeport | 40 Huntington Turnpike, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-10-03 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | homeowner called | unknown | NA | No |  | 2024-10-03 | 02:00 PM | Unknown | 100 |  | surcharged main line clean with high velocity jet/vactor - rag ball in line | Bridgeport | 97 Alfred St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-08-18 | 12:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 1.48" rain | plant flow meter | 1.76MG | plant flow meter | Yes | Bridgeport harbor | 2024-08-18 | 03:45 PM | 1.76MG | 1760000 |  | weather event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-06 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | plant flow meter | 2.55MG | flow meter | Yes | Long Island Sound | 2024-08-06 | 11:30 PM | 2.55MG | 2550000 |  | wet weather event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-06 | 07:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Main line surcharged due to grease | Homeowner called in | unknown | NA | No |  | 2024-08-06 | 08:45 PM | unknown | 100 |  | jet vac, cleared main line surcharge | Bridgeport | 344 W Morgan Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-07-25 | 03:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Rags and grease | Home owner notified the fire dept who notified the WPCA | 500 gallons | visual determination | No |  | 2024-07-25 | 04:45 PM | 500 gallons | 500 |  | Main line was jetted and area was cleaned up | Bridgeport | 69 Goddard Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-07-17 | 07:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Flow meter and street level indicator | 1.46 mg. | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2024-07-17 | 09:45 PM | 1.46mg. | 1460000 |  | Rain ended and influent flow decreases. Plant resumed normal operation | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-06-30 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 0.41" rain in short period | flow meter | 0.71MG | flow meter | Yes | Bridgeport Harbor, Long Island Sound | 2024-06-30 | 06:30 PM | 0.71MG | 710000 |  | weather event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-06-10 | 10:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Home owner notified the Bridgeport WPCA | N/A | N/A | No |  | 2024-06-10 | 11:15 AM | N/A | 100 |  | personnel jetted main line and cleared blockage | Bridgeport | 767 Capitol Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-05-29 | 08:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags | Call to the WPCA | Unknown | N/A | Yes | Rooster River / Ox brook | 2024-05-29 | 09:45 AM | Unknown | 100 |  | Field operations personnel responded and found grease and rags clogging the main line. Personnel used the jetter truck to clear the line. Area was cleaned. Line was flowing properly by 9;50am. | Bridgeport | 757 Madison Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-05-27 | 04:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | High flows and heavy rain | Street level indicator and flow meter | N/A | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2024-05-27 | 07:30 PM | 1.57mg | 1570000 |  | Heavy rain stopped and plant resumed normal operation | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-04-26 | 03:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | A combination of grease , rags and roots caused the bypass | Citizen notified the WPCA | unable to determine | visual deternination | Yes | Long Island Sound | 2024-04-26 | 05:30 PM | N/A | 300 |  | Field Operations personnel jetted the main line and removed debris. Then cleaned up the area | Bridgeport | 100 Kossuth St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-03 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Flow meter and street level indicator | 3.69mg. | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2024-04-04 | 01:15 AM | 3.69 | 3690000 |  | Heavy rain ended flow decreased and plant resumed normal operations | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-28 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | Flow meter / street level indicator | N/A | N/A | Yes | Bridgeport Harbor / Long Island Sound | 2024-03-28 | 06:15 AM | 1.63 MG | 1630000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-23 | 11:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | Flow meter / street level | N/A | N/A | Yes | Bridgeport Harbor / Long Island Sound | 2024-03-23 | 11:30 PM | 5.99 MG | 5990000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2024-03-12 | 09:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease | Homeowner notified the Bridgeport WPCA | 200 gallons | Visual determination | Yes | Seeley Pond | 2024-03-12 | 10:00 AM | 200 gallons | 200 |  | Field operations' staff jetted the main line and cleared grease blockage. area was also cleaned. | Bridgeport | 369 Hawley Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-09 | 09:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain and high flows | Flow meter and street level indicator | N/A | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2024-03-10 | 09:00 AM | 4.57 mg. | 4570000 |  | Heavy rain stopped and plant resumed normal operation | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-06 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Flow meter and street level indicator | NA | flow meter | Yes | Bridgeport Harbor | 2024-03-07 | 03:30 AM | 3.65 mg. | 3650000 |  | Heavy rain ended and flows decreased. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-13 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain/high flows | Street level indicator/flow meter | N/A | N/A | Yes | Bridgeport Harbor/Long Island Sound | 2024-01-13 | 03:15 PM | 5.44mg | 5440000 |  | Rain ended and flow decreased | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-09 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain / high flows | Street level indicator / flow meter | n/a | n/a | Yes | Bridgeport Harbor / Long Island Sound | 2024-01-10 | 06:15 AM | 4.96 MG | 4960000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2024-12-27 | 01:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by resident | 580 gal | Visual | Yes | Black Rock Harbor | 2024-12-27 | 02:15 PM | 580 gal | 580 |  | event ended | Bridgeport | 84 Bryant St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-12-17 | 01:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual | N/A | N/A | Yes | Cedar creek Long Island sound | 2024-12-17 | 04:00 AM | 3.02 mg | 3020000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-11-28 | 11:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2024-11-28 | 05:30 PM | 4.31 MG | 4300000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-11-22 | 01:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | plant flow meter | pending | plant flow meter | Yes | Cedar Creek Long Island Sound | 2024-11-22 | 05:30 AM | 4.43 MG | 4430000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-08-18 | 09:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | N/A | N/A | N/A | Yes | Cedar creek Long Island Sound | 2024-08-18 | 05:30 PM | 5.98 mg | 5980000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-18 | 10:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 2.03" rain | flow meter | 5.32MG | certified flow meter | Yes | Bridgeport Harbor | 2024-08-19 | 02:45 AM | 5.32MG | 5320000 |  | weather event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-06 | 05:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | plant flow meter | 10.2MG | plant flow meter | Yes | Long Island Sound/ Bridgeport Harbor | 2024-08-07 | 01:15 AM | 10.2MG | 10200000 |  | wet weather event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-07-17 | 07:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observations | N/a | N/a | Yes | Cedar creek Long Island sound | 2024-07-18 | 03:45 AM | 6.92 MG | 6922222 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-13 | 08:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual | N/A | N/A | Yes | Cedar creek Long Island sound | 2024-07-13 | 01:30 PM | 4.57 mg | 4570000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-06 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | N/A | N/A | Yes | Cedar creek Long Island Sound | 2024-07-06 | 01:00 PM | 3.17 mg | 3170000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2024-06-22 | 12:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Main line surcharge, grease, rags | Homeowner called in | Unknown | NA | No |  | 2024-06-22 | 02:30 PM | Unknown - private basement | 100 |  | Main line cleared of grease | Bridgeport | 476 Brooklawn Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-06-14 | 08:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Monitoring Equipment | 4.28MG | Flow meter | Yes | Bridgeport Harnor | 2024-06-14 | 11:30 PM | 4.38MG | 4380000 |  | rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-05-27 | 05:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain | Visual | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2024-05-27 | 08:15 PM | 4.6 MGD | 4600000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2024-05-14 | 03:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease in invert | resident called in | 100gal | visual | No |  | 2024-05-14 | 03:30 PM | 100gals | 100 |  | Line pressure jetted and vacuumed clear, road surface cleaned and vacuumed | Bridgeport | 80 Logan St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-03 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain fall | flow meter / street level indicator | N/A | N/A | Yes | Cedar Creek / Long Island Sound | 2024-04-04 | 04:45 AM | 10.35 MG | 10350000 |  | Storm event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-28 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | West Side went into permitted secondary bypass due to heavy rain 3:30am. | visual observation | n/a | n/a | Yes | cedar creek long island sound | 2024-03-28 | 08:45 AM | 2.985 MGD | 2985000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-23 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2024-03-24 | 03:00 AM | 8.96 MGD | 8960000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-09 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Flow meter and street level indicator | N/A | Flow meter | Yes | Cedar Creek / Long Island Sound | 2024-03-10 | 02:00 PM | 7.54 MG | 7540000 |  | Rain event ended. | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-06 | 05:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2024-03-07 | 10:30AM | 13.53 MGD | 13530000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-02 | 03:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain/ high flows | street level indicator / flow meter | N/A | N/A | Yes | Cedar Creek / Long Island Sound | 2024-03-03 | 00:30 AM | 6.56 MG | 6560000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-02-27 | 10:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain / High flows | Street level indicator and flow meter |  |  | Yes | Cedar Creek / Long Island Sound | 2024-02-28 | 02:30 AM | 3.26 MG | 3260000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-01-28 | 07:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation |  |  | Yes | cedar creek long island sound | 2024-01-28 | 02:45 PM | 4.17 | 4170000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-01-13 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain / high flows | street level indicator / flow meter | N/A | N/A | Yes | Cedar creek / Long island sound | 2024-01-13 | 04:30 PM | 12.7 MG | 12700000 |  | Rain event ended. | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-01-09 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain fall | Visual observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2024-01-10 | 11:15 AM | 9.55 MG | 9550000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
[17 empty] | TOTAL VOLUME | 176700052

## BRISTOL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 04:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Excessive rain. Two 20" main sewer lines were surcharged to pump station. Flow exceeded pipes capacity. | Resident at 15 Trout Brook called in a possible stoppage. Crew found main sewer lines surcharged from Stevens Street to Broad Street. | Based on picture received from crew. estimate 25 gpm. | Based on conversation with crew and provided picture of the bypass | Yes | Copper Mine Brook | 2024-01-14 | 01:00 AM | 31,500 gallons | 31500 |  | Flow subsided from storm event | Bristol | 1001 Stafford Ave, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-10 | 01:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Due to the storm event, 24" main sewer line exceeded its capacity. | visual inspection of the line. | Estimate a discharge rate of 25 gpm. | estimated based on visual inspection. | Yes | Bristol Fish and Game Club Pond | 2024-01-10 | 09:00 PM | 30,000 gallons | 30000 |  | Yes | Bristol | 50 Downs St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-12-10 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Debris in the main line (clay pipe piece, process, rocks, silt). | Received a call from a resident about a possible issue in the main line. | Roughly 25 gpm estimated. Bypass in the form of Bypass Pumping from the MH at the Intersection of Evelyn Rd and Poitras Rd to another Bristol MH on Poitras Rd in Bristol that eventually leads to Plainville WPCF's collection system. | Estimated based on pump output. | No |  | 2024-12-12 | 03:00 PM | Estimate of 25 gpm for a total of 56 hours= 84,000 gallons as an estimate. | 84000 |  | Main line was excavated to a lateral tie in for inspection and access. Line was cleaned from all directions. | Bristol | 57 Evelyn Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-03-13 | 10:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Bypass was due to a build up of rags and grease around broken clay pipe. | Staff received a possible stoppage call from homeowner at 25 Wooding Street | 300 gallons, based on homeowner description of quantity in basement. | based on homeowner description of quantity in basement. | No |  | 2024-03-14 | 08:30 AM | 300 gallons | 300 |  | Yes | Bristol | 25 Wooding St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-12-27 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | bypass was from grease in the line approximately 100ft upstream of manhole 24-181 | Received call from City of Bristol Housing Authority regarding manhole in front of 66 Vance Drive being wet around manhole. | 5 to 10 gallons. | based on visual inspection upon arrival. | No |  | 2024-12-27 | 11:30 AM | 5-10 gallons | 8 |  | Yes, line jet cleaned. blockage removed. | Bristol | 56 Vance Dr, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-03-03 | 12:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Build up of grease, rags and rocks. | Received call from resident at 133 Central Street | 5 gpm | visual inspection at arrival | No |  | 2024-03-03 | 01:30 PM | estimated quantity is between 50 to 100 gallons | 90 |  | yes | Bristol | 133 Central St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-06-03 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Buildup of grease and rags in the main sewer line 30 feet from the intersection of Marconi Avenue and Peck Lane. | Received a call from the City of Bristol Water department. | 50 to 100 gallons | Quantity is based on the rate of discharge upon arrival and length of time bypass occurred. | No |  | 2024-06-03 | 10:30 | 100 gallons | 100 | Based on rate and length of discharge. | Staff jetted the line, removing sewer blockage. | Bristol | 12 Marconi Ave, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2024-02-26 | 12:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | buildup of rags and grease 220 ft from manhole 24-180 | Recieved a possible stoppage call from resident at 68 Vance Drive | 10 gpm | visual inspection upon arrival | No |  | 2024-02-26 | 12:30 | 15 gallons | 15 | Based on rate and length of discharge. | Staff Jetted the line and removed blockage. | Bristol | 171 Vance Dr, Bristol, CT
[17 empty] | TOTAL VOLUME | 146013

## CHESHIRE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
CHESHIRE | Closed | Sewage Bypass | Snowmelt | 2024-01-15 | 00:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Our 16 inch force main cracked, we have now completed a bypass of the broken section | Cheshire PD and regional water notified me of water bubbling from under the sidewalk | 200 GPM | visual | Yes | mill river | 2024-01-22 | 06:00 PM | 2 million gallons estimated | 2000000 |  | Larosa Construction installed a 12inch bypass line tied in prior to line break and put back into force main after the break, they will repair the break and remove bypass line. | Cheshire | 906 S Main St, Cheshire, CT
CHESHIRE | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-01-10 | 07:30 PM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | plant filled to capacity | inspecting the streets following a storm such as this. we found wastewater breaching a manhole on Riverside Dr, in cheshire | <1000 gallons | visual inspection | No |  | 2024-01-11 | 02:00 AM | 3000 | 3000 |  |  | Cheshire | Riverside Dr, Cheshire, CT
[17 empty] | TOTAL VOLUME | 2003000

## COVENTRY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
COVENTRY | Closed | Sewage Bypass | Dry | 2024-03-12 | 08:00 AM | Treatment Plant | Partially Treated Raw Sewage | Other | all infiltration basins are full. Basin 8 overflowing. | Operators discovered bypass during daily checks at 8 AM. | estimated 5,000 gallons per hour | flow is approx 10,000 gallons per hour but half of it infiltrates into basins naturally. | No |  | 2024-03-12 | 10:00 AM | 10,000 gallons | 10000 |  | operators switched basins | Coventry | 394 Main St, Coventry, CT
COVENTRY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-11 | 08:00 AM | Treatment Plant | Partially Treated Raw Sewage | Other | Infiltration Basin #7 overflowed. All of the basins are full. | Operators discovered overflow during daily plant checks. | 27,000 gallons | Estimated based on flow meter readings 8 AM - 10 AM. | No |  | 2024-03-11 | 10:00 AM | 27,000 gallons | 27000 |  | Operators switched effluent to other basins and basin 7 drained down slowly. | Coventry | 394 Main St, Coventry, CT
COVENTRY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-07 | 01:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Infiltration Basins are all full and basin 7 overflowed. | Operators discovered overflow during daily inspection of basins. | 21,000 gallons | influent flow meter readings | No |  | 2024-03-07 | 02:00 AM | 21,000 gallons | 21000 |  | flow went down as rainfall subsided | Coventry | 394 Main St, Coventry, CT
[17 empty] | TOTAL VOLUME | 58000

## CROMWELL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-08-19 | 08:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened Bypass gate | Plant influent was ~63 MGD at the time opening bypass gate | Using the difference between calibrated influent and effluent parshall flume | Yes | CT river | 2024-08-20 | 06:00 AM | 2,466,040 gallons of disinfected partially treated effluent, combined with 21,541,232 gallons of fully treated effluent during the 9.5 hour event. | 2466040 |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-08-18 | 10:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator Opened Bypass gate | Plant influent was approximately 75 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent Parshall flume. | Yes | Connecticut River | 2024-08-19 | 01:00 PM | 4,821,250 gallons of disinfected partially treated effluent, combined with 33,380,625 gallons of fully treated effluent during the 14.25 hour event. | 4821250 |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-06-30 | 07:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 70 MGD at time of opening bypass gate | Using the difference between the calibrated influent and effluent Parshall flume | Yes | Connecticut River | 2024-06-30 | 10:15 PM | 462,915 gallons of partially treated effluent, combined with 6,547,273 gallons of fully treated effluent during the 2.75 hour event. | 462915 |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-04 | 01:45 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate | Plant influent was approximately 62 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2024-04-04 | 09:45 PM | 6,824,972 gallons of partially treated effluent, combined with 46,824,813 gallons of fully treated effluent during the 20 hour event. | 6824972 |  | When flow subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 07:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator Opened Bypass Gate | Plant influent was approximately 80 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2024-03-24 | 08:30 AM | 6,093,742 gallons of partially treated effluent, combined with 30,392,879 gallons of fully treated effluent during the 13 hour event. | 6093742 |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-09 | 11:45 PM' | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 58 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2024-03-11 | 03:30 PM | 21,696,875 gallons of partially treated effluent, combined with 93,031,562 gallons of fully treated effluent during the 39.75 hour event. | 21696875 |  | When flow subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 10:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 58 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2024-03-08 | 06:15 PM | 24,052,896 gallons of partially treated effluent, combined with 102,243,141 gallons of fully treated effluent during the 44 hour bypass. | 24052896 |  | When plant flows subsided under 55 MGD operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 06:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate | Plant influent was approximately 70 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes | Yes | Connecticut River | 2024-01-14 | 04:00 AM | 10,404,901 gallons of partially treated effluent, combined with 50,477,709 gallons of fully treated effluent during the 21.58 hour event. | 10404901 |  | When plant flows subsided under 55 MGD operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Dry | 2024-01-10 | 01:15 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Rain on top of snow melt created higher than normal flow in trunkline. Ground was already saturated. | Inspection of main sewer line after rain and snow melt event. | 25 gallons per minute x 4 manholes in a row x 720 minutes = 72,000 gallons total | Estimated visually | Yes | Mattabesset River and Willow Brook | 2024-01-11 | 01:15 AM | 72,000 gallons overflow | 72000 |  | Flows subsided | Berlin | 376 Berlin Turnpike, Berlin, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-10 | 01:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 85 mgd at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2024-01-12 | 00:30 AM | 36,871,751 gallons of partially treated effluent, combined with 110,001,713 gallons of fully treated effluent during the 47.5 hour event. | 36871751 |  | When plant flows subsided under 55 MGD operator closed bypass gate. | Cromwell | 245R Main St, Cromwell, CT
[17 empty] | TOTAL VOLUME | 71401548

## DANBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DANBURY WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator on Duty | 4.998 MG | Flow data recorded during duration of bypass event | No |  | 2024-08-19 | 07:00 AM | 4.998 MG | 4998000 |  | Flows dropped below the Equalization tank set point allowing all flow to proceed to secondary treatmenty | Danbury | 53 Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2024-01-20 | 02:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease in main line | Homeowner | 500gal | Visual Estimate | No |  | 01/23/2024 | 03:00 PM | 500gal | 500 | Visual Estimate | jetted line and Permanganate | Danbury | 16 Dibble St, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 06:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator on Duty | 2920000 | Flow meter readings and duration of bypass | No |  | 2024-01-10 | 06:00 PM | 2920000 | 2920000 |  | Storm event ended and flows returned to normal | Danbury | 53A Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2024-01-03 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  |  | 250-500gal | Visual Estimate | No |  | 01/03/2024 | 11:00 AM | 200-500gal | 350 | Visual Estimate | Jetted the line and added permanganate | Danbury | 10 Old Sherman Turnpike, Danbury, CT
[17 empty] | TOTAL VOLUME | 7918850

## DARIEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DARIEN | Closed | Sewage Bypass | Dry | 2024-12-01 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | hole in pipe. | Police notified Parks and Rec and P&R notified DPW | 50 GPM | Visual estimation | No | Long Island sound (Weed Beach)bypass contained, collected and properly disposed of in City of Stamford wastewater collection system. (DJO changed to "No" to reaching waterbody).less than 50 gallons reached CB's, hard surfaces were cleaned and CB's pumps p | 2024-12-02 | 02:00 AM | 42,000 gallons, all of which was collected and disposed of in City of Stamford Waste Water Collection System. | 0 |  | Band clamp installed over hole | Darien | 159 Nearwater Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 06:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | reported | 1 GPM | visual estimate | Yes | goodwives river | 2024-03-23 | 08:30 PM | 120 | 120 |  | cessation of precip | Darien | 2 Sedgewick Village Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-10 | 01:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Notified by police | Approx 5 gallons per minute | Visual estimation | Yes | Goodwives River | 2024-03-10 | 04:45 AM | 226 gallons | 226 |  | rain subsided. | Darien | 7 Sedgwick Ave, Darien, CT
[17 empty] | TOTAL VOLUME | 346
*The 12/1/24 incident is counted as a bypass but has a zero for volume as all sewage was contained and placed back into the system
The incident is included here to show that they were reported in good faith.

## DERBY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DERBY | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 11:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visually observed during emergency call in. | 52,083 | Calculation based on the observed flow of 2.5 MGD for the span of 30 minutes. | Yes | Housatonic | 2024-08-19 | 00:00 AM | 50,000-75,000 gallons | 70000 |  | Public works department called into to turn on combined effluent pumping station | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2024-08-15 | 11:30 AM | Treatment Plant | Sludge Spill | Other | Over filled sludge blend tank | Visually by operator | 50-100 gallons | Visually | No |  | 2024-08-15 | 01:00 PM | 50-100 gallons | 90 |  | Stopped pumping sludge into blend tank and cleaned sludge sill in parking lot. | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2024-05-01 | 04:45 AM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | Our back up aeration blower not running. Main blower is out of service waiting on repairs. A crew is on their way to the plant. | Auto dialer alarm | 25,000 - 50,000 gallons | visual of effluent discharge | Yes | Housatonic River | 2024-05-01 | 05:15 AM | Between 25,000 & 50,000 | 40000 |  | The blower tripped out due an issue with the harmonic guard. The harmonic guard was by-passed breaker was reset. | Derby | 1 Caroline St, Derby, CT
[17 empty] | TOTAL VOLUME | 110090

## EAST HADDAM
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST HADDAM WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-12-16 | 04:15 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure |  | Lack of flow to main treatment plant observed by operator | 5 - 10,000 gallons estimated total | As compared to normal flows to the treatment plant for that time period. | Yes | Connecticut River | 2024-12-18 | 10:00 AM | 10,000 gallons | 10000 |  | Broken clogged pipe was repaired | East Haddam | 1 Dock Rd, East Haddam, CT
[17 empty] | TOTAL VOLUME | 10000

## EAST HARTFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-12-01 | 11:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | GREASE AND SOFT BLOCKAGE PAPER AND RAGS. | HOMEOWNER | < 1OOg | Visual Observation by MDC Personnel | No |  | 2024-12-02 | 04:00 AM | < 1OO gal | 85 |  | JET TRUCK FLUSHED MAIN SEWER. | East Hartford | 65-67 Columbus St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-03 | 09:00 AM | Basement | Raw Sewage | Unknown |  | MDC PERSONNEL | <10g | MDC PERSONNEL | No |  | 2024-04-03 | 09:15 AM | <10g | 9 |  | JET TRUCK RELIEVED MAIN SEWER. | East Hartford | 236 Main St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-02-14 | 12:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Other |  | MDC Personnel | <100g | MDC Personnel | No |  | 2024-02-14 | 12:30 PM | Less than a half gallon. | 1 |  | Jet truck relieved M/S | East Hartford | 475 Burnside Ave, East Hartford, CT
[17 empty] | TOTAL VOLUME | 95

## EAST HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-08-02 | 09:00 AM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | Called in by property owner | less than 5 gallons | Field estimate by crew | No |  | 2024-08-02 | 10:15 AM | less than 5 gallons | 5 |  | line was jetted and cctv inspected, pipe to be excavated and repaired 8-5-2024, pipe is currently open and flowing normally. | East Haven | 33 Andys Dr, East Haven, CT
[17 empty] | TOTAL VOLUME | 5

## EAST LYME
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST LYME | Closed | Sewage Bypass | Dry | 2024-09-17 | 03:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Sewage in road | 208 GPM | Average Daily Flow of Bridebrook Wastewater Pump Station | Yes | Bride Brook | 09/17/2024 | 05:30 PM | 31,200gal | 31200 | 208gpm average over 2.5 hours | Force main was repaired with repair band | East Lyme | 255 W Main St, East Lyme, CT
[17 empty] | TOTAL VOLUME | 31200

## FAIRFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-12-30 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | GREASE | Called in by WPCF personnel | 75 Gallons | visual estimate | No |  | 2024-12-30 | 12:30 PM | 75 Gallons | 75 |  | Jetted line to break blockage | Fairfield | 199 Bronson Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-12-25 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Service request sent in by resident | 400 gallons | visual estimate | No |  | 2024-12-25 | 10:30AM | 400 gallons | 400 |  | jetted line to break plug and remove rag blockage | Fairfield | 15 Pine Tree Ln, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-10-28 | 10:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | Root blockage in town line | Resident notified the Sewer department | 100 gallons | Visual guestimate | No |  | 2024-10-28 | 11:15 AM | 100 gallons | 100 |  | flushed line | Fairfield | 360 Tunxis Hill Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-09-18 | 07:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | removed a broken manhole cover frame blocking invert | Called in by DPW | 200 gallons | visual estimate | No |  | 2024-09-18 | 08:45 AM | 200 gallons | 200 |  | Flushed line and removed debris from invert . | Fairfield | 269 Linley Dr, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-08-07 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Homeowner called into Sewer Inspectors office. | 5 gallons | visual estimate | No |  | 2024-08-07 | 02:00 AM | 5 gallons | 5 |  | Line was flushed and cleared of root mass. | Fairfield | 20 Greenlawn Dr, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-06-02 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by ECC | 75 Gallons | Visual estimate | No |  | 2024-06-02 | 11:45 AM' | 75 Gallons | 75 |  | Jetted the line to break blockage | Fairfield | # 608 Kings Hwy W, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-04-16 | 02:30 PM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | homeowners leaking curb box | Revize service request | 5 gph | visual estimate | No |  | 2024-04-17 | 06:30 PM | 1500 gallons | 1500 |  | Repair was made to the curb box . | Fairfield | 945 Sasco Hill Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-04-03 | 08:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm event inspections | 5000 gallons | visual estimate | No |  | 2024-04-04 | 00:15 AM | 5000 gallons | 5000 |  | event ended | Fairfield | 122 Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-04-03 | 09:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm event inspections | 1000 GALLONS | visual estimate | No |  | 2024-04-04 | 00:15 AM | 1000 gallons | 1000 |  | storm ended | Fairfield | 133 Berwick Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-23 | 05:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | heavy rains | inspections | 30,000 gallons | visual estimate | No |  | 2024-03-24 | 11:45 PM' | 30,000 | 30000 |  | flows subsided. | Fairfield | Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-23 | 07:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm event inspections | 500 gallons | visual estimate | No |  | 2024-03-25 | 01:00 AM | 500 gallons | 500 |  | storm charge went down | Fairfield | # 192 Lynnbrook Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-10 | 03:00 AM | Select... | Raw Sewage | Excessive Flows - Storm Event |  | storm event inspections | 5500 gallons total from four locations | visual estimate | No |  | 2024-03-10 | 11:45 PM' | 5500 gallons total | 5500 |  | rain event ended | Fairfield | Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-10 | 00:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Heavy rains | Inspections | 10,000 gallons total from all bypassing man holes | visual estimate | No |  | 2024-03-11 | 11:00 PM | 10,000 gallons total out of all bypassing man holes | 10000 |  | rain event ended | Fairfield | Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 06:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | rain event inspections | 5000 gallons | visual estimate | No |  | 2024-01-14 | 06:00 AM | 5000 gallons | 5000 |  | rain event ended | Fairfield | 172 Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 09:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm Event inspections | 2000 gallons total | visual estimate | No |  | 2024-01-14 | 06:00 AM | 2000 gallons total | 2000 |  | rain event ended | Fairfield | 500 Grasmere Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 02:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm event inspections | Grasmere ave & Kings hwy cut off : 3000 gals ,# 178 Halley ave : 7000 gals , # 207 Rutland ave : 1000 gals . | visual estimate | Yes | ash creek | 2024-01-11 | 04:00 AM | 11000 gallons total | 11000 |  | storm ended | Fairfield | 330 Richard White Way, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 02:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | inspections | 5000 gallons total for two locations | visual estimate | No |  | 2024-03-07 | 11:45 PM' | 5000 gallons total from two locations | 5000 |  | rain event ended | Fairfield | Halley Ave, Fairfield, CT
[17 empty] | TOTAL VOLUME | 77355
75000

## GLASTONBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GLASTONBURY | Closed | Sewage Bypass | Dry | 2024-01-06 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident call | 2 gallons per minute for 2 hours. 240 gallons total | estimated 2 gallons per minute flowing from manhole | No | Reached a drainage swale along route 2. | 2024-01-06 | 03:00 PM | 240 gallons | 240 |  | Flusher truck removed grease blockage. | Glastonbury | 29 Deming Rd, Glastonbury, CT
[17 empty] | TOTAL VOLUME | 240

## GRANBY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GRANBY | Closed | Sewage Bypass | Dry | 2024-09-15 | 03:00 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Pump failure at Pump Station. | Call from a Granby resident to the Town of Granby DPW director (Kirk Severance). Kirk, then called the Granby Police Department to verify the problem. Once onsite the police department confirmed the problem. | Estimated quantity is about 50 gallons. | Visual estimation used. | No | West Branch Salmon Brook. | 2024-09-15 | 05:00 PM | Estimated quantity is about 50 gallons. | 50 |  | Dirt was used to fill the swale, stopping the sewage flow from entering the local brook, and the flow ceased. | Granby | 166 Salmon Brook St, Granby, CT
[17 empty] | TOTAL VOLUME | 50

## GREENWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2024-07-12 | 11:00 AM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | There was a break (large crack) in the sanitary sewer low pressure pump line for 55 Hillcrest Park Road near the private storm drainage network. See Attached photos. | Received complaint of sewer odors from a property owner in the area | Unknown | N/A - as could not be determined | Yes | A portion of sanitary sewer flow drained through the soil into a stone drainage culvert which eventually ends up in a pond on private property. | 2024-08-02 | 01:00 PM | Unknown. | 100 |  | Performed a point repair to replace approximately 9.5 feet of private low pressure sanitary sewer pump line. | Greenwich | 59 Hillcrest Park Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2024-05-24 | 08:45 AM | Treatment Plant | Partially Treated Raw Sewage | Other | Maintenance activity to the low level sensor on the UV channel caused all power to the UV bulbs to be turned off for a period of 11 minutes | After the maintenance activity was completed, all three banks came online because the system was in alarm, which led to further investigation. | 61,000 gallons of treated by not disinfected effluent | 11 min (8:48am-8:59am) at 8MGD, approximately 61,000 gallons discharged with no disinfection | Yes | Greenwich Harbor | 2024-05-24 | 09:00 AM | 61,000 gallons discharged with no disinfection | 61000 |  | The UV system panel was reset and resumed normal operation. | Greenwich | 250A Shore Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Other | 2024-01-10 | 09:45 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Heavy rains overnight (2.5-inches) combined with snow melt and previously saturated ground | Visual inspection of collection system | Unknown at this time | N/A | Yes | Horseneck Brook | 2024-01-11 | 01:45 PM | Final quantity cannot be determined. However, during the peak flow the overflow could have been approximately 200 gpm and as flows receded the quantity was significantly less. | 200 |  | Weather improved and flows subsided. | Greenwich | 84 Brookside Dr, Greenwich, CT
[17 empty] | TOTAL VOLUME | 61300

## GROTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2024-12-24 | 01:30 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure |  | reported through the public observation | 25gph | How much it filled a 5-gallon bucket over 10 min | No |  | 2024-12-12 | 02:30 PM | 25 gallons | 25 | How much it filled a 5-gallon bucket over 10 min | replaced tap that was leaking/cracked. | Groton | 5 Beach Pond Rd, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2024-09-19 | 08:30 PM | Manhole | Raw Sewage | Unknown | Clog in downstream line | Called in through residents | 0.5 gallon per minute overflowing for an hour total quantity of 30gallon | visual determination | No |  | 2024-09-19 | 09:30 PM | 30 gallons | 30 |  | Jetted downstream line | Groton | 7 Eastern Point Rd, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-07-29 | 07:15 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Gasket blew out | Contractor found leak | unknown | visual estimation.More flow came out, but it mostly went into a plugged catch basin due to the construction. We pump out the catch basin batch back to the sewers. only a small amount missed the catch basin and went into the ground. | No |  | 2024-07-29 | 01:30 PM | 300 gallons | 300 |  | replaced gasket and drained force main back to the pump station | Groton | 197 Shore Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2024-07-11 | 10:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Brick in down stream collection system | Called in from resident | 30 gallons | Personnel on site say flow volume and duration | No |  | 11/07/2024 | 11:30 AM | 30 gallons | 30 | Estimated by amount collected in vac truck | Jetted line to remove blockages | Groton | 107 Spicer Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2024-03-10 | 09:00 PM | Pump Station | Raw Sewage | Electrical Equipment Failure | Lost a phase of power coming into the pumpstation and the backup generator didn't automatically come on. My employee was already on site and troubleshooting the issue of the backup generator. Eventually we were able to get the generator to start up but t | The Wet well gave a high alarm code to our on call man. | 63 gpm for 10 minutes. total of 630 gpm | The pumps have hour meters on them using yesterday flow we received a total of 91200 gallons throughout the day. If you calculate it down to minutes, it comes out to 63 GPM. | Yes | Thames river | 2024-03-10 | 09:15 AM | 630gpm | 630 |  | started the backup generator in hand and had grid power fixed a few hours later. | Groton | 51 Fairview Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2024-02-08 | 07:00 AM | Pump Station | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | rags | Daily Pump station check | Current discharge rate at about 1GPM | Flow through manhole lid hole | No |  | 2024-02-08 | 12:30 PM | 330 gal | 330 |  | Jetted line | Groton | 149 Nathan Hale Rd, Groton, CT
GROTON, TOWN OF | Closed |  | Rain less than 1" per hour | 2024-07-15 | 00:00 AM | Manhole | Disinfected Partially Treated Raw Sewage | Unknown | Cause unknown. | Resident contacted water company. Water company determined it was sewage. | 2 gal/minute | See video | No |  | 2024-07-15 | 00:00 AM | Unknown | 100 |  | It stopped before we knew about it | Groton | 56 Shennecossett Pkwy, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2024-01-23 | 08:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Fat oil and grease buildup | Beacon Point Homes called in bypass. | UNK. Spill backed up into building. | UNK | No |  | 2024-01-23 | 09:00 AM | 5 gallons. | 5 |  | Line cleared. | Groton | 26 Highland Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2024-05-13 | 07:30 AM | Sewer Main | Raw Sewage | Unknown | Valve supposed to be shut off by sailors but was not properly shut off. User error. | Sailors noticed while clearing sewage from ship. Reported incident to Port Ops. | Approximately 5 Gal. | UNK at this time. | No |  | 2024-05-13 | 09:30 AM | .5 Gallons | 5 |  | Port Ops cleaned up sewage and disposed of materials properly. | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-05-05 | 06:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | N/A | FM&S WS, Alec Brown Reported to Utilities Maintenance Supervisor (Mathew Tellier). | 20 gallons. | Visual. | No | N/A | 2024-05-05 | 09:00 PM | 5 gallons. | 5 |  | Line cleared. | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2024-02-21 | 03:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | N/A | Call went to Public Works Dept. about an overflowing manhole. | 10-100 gallons to Driftwood lane. | Supervisor estimate, none to Storm drains and ground was frozen so no seeping in. | No | N/A | 2024-02-21 | 03:30 AM | 10-100 gallons. | 90 |  | Cleared the roots--Note: a contractor apparently cleared roots in the lateral lines last week with a snake, they may have flowed down to the main and caused blockage. UEM removed the roots, line flowing properly. | Groton | 154 Driftwood Cir, Groton, CT
[17 empty] | TOTAL VOLUME | 1550

## HARTFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-12-17 | 02:45 AM | Basement | Raw Sewage | Unknown |  | CUSTOMER CALLED MDC COMMAND CENTER | LESS THAN 100 GAL | MDC PERSONNEL | No |  | 2024-12-17 | 05:30 AM | LESS THAN 100 GAL | 90 |  | MDC JETTED MAIN SEWER BLOCKAGE RELIEVED | Hartford | 311 Linnmoore St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-10-07 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | M/S BACKED UP DUE TO GREASE | CUSTOMER CALL | LESS THAN 10 GALLONS | MDC PERSONNEL | No |  | 2024-10-07 | 07:00 PM | LESS THAN 10 GAL. | 9 |  | JET TRUCK RELIEVED BLOCKAGE. | Hartford | 248 Sisson Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-09-10 | 01:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | SEWER MAIN COLLAPSE | CAVITY FORMED IN THE ROAD | NO SPILL - BYPASS PUMP OPERATION ONLY | NO SPILL - BYPASS PUMP OPERATION ONLY | No |  | 2024-09-10 | 06:00 PM | 8000 GALLONS PUMPED NO SPILL - BYPASS PUMP OPERATION ONLY | 0 |  | MDC REPAIR CREW FIXED COLLAPSED MAIN SEWERNO SPILL - BYPASS PUMP OPERATION ONLY | Hartford | 52 Curtiss St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 06:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT SURCHARGED | MDC PERSONELL | <100G | MDC PERSONNEL | No |  | 2024-08-19 | 07:30 AM | < 100 | 90 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 442 New Britain Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 06:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER SURCHARGE | MDC PERSONNEL | <100G | MDC PERSONNEL | No |  | 2024-08-19 | 07:30 AM | < 100 | 90 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 79 South St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT SURCHARGE | MDC PERSONNEL | <100G | MDC PERSONNEL | No |  | 2024-08-19 | 07:30 AM | < 100 | 90 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 87 Stone St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 07:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT SURCHARGE | MDC PERSONNEL | <100G | MDC PERSONNEL | No |  | 2024-08-19 | 07:30 AM | < 100 | 90 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 14 Chapin Pl, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-08-03 | 11:15 AM | Sewer Main | Raw Sewage | Other | CONTRACTOR HIT WATER MAIN CAUSING WATER MAIN BREAK. | MDC SCADA SYSTEM | > 100,000 GALLONS | MDC SCADA SYSTEM | Yes | Park River Conduit | 2024-08-03 | 12:45 PM | .133 MG | 133000 |  | WATER MAIN SHUT DOWN. | Hartford | 402 Asylum St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-07-17 | 10:30AM | Sewer Main | Raw Sewage | Other | CONTRACTOR WORKING IN CSO CHAMBER | SCADA | < 20,000 GALLONS | SCADA | Yes | PARK RIVER CONDUIT | 2024-07-17 | 11:30 AM | 11, 000 GALLONS | 11000 |  | ONCE CONTRACTOR COMPLETED THE WORK | Hartford | Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-06-13 | 09:00 AM | Sewer Main | Raw Sewage | Other | Contractor working on sewer line | MDC SCADA System | <100,000g | MDC SCADA System | Yes | Park River Conduit | 2024-06-13 | 12:30 PM | 36000gal | 36000 |  | CONTRACTOR FINISHED WORK OVERFLOW ENDED | Hartford | 450 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-05-18 | 12:15 PM | Basement | Raw Sewage | Unknown |  | PLUMBER CONTACTED MDC REPORTING BACK UP IN BASEMENT | LESS THAN 100 GAL | MDC PERSONEL | No |  | 2024-05-18 | 03:00 PM | 100-200 GAL | 150 |  | MDC CREW JETTED MAIN SEWER RELIEVING BLOCKAGE | Hartford | 80 Charter Oak Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 08:00 AM | Manhole | Raw Sewage | Unknown | COLLAPSED MAIN SEWER | CALL FROM HFD DISPATCH | LESS THAN 100 GAL | MDC PERSONEL | No |  | 2024-03-23 | 05:45 PM | 2000G | 2000 |  | MDC REPAIR CREW REPAIRED MAIN SEWER | Hartford | 50 Stonington St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 05:30 PM | Select... | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | PASSER BY | <100G | MDC PERSONNEL | Yes | SOUTH BROOK PARK RIVER | 2024-03-24 | 05:30 AM | <100G | 90 |  | BYPASS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | Hartford | 150 New Park Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 04:45 PM | Basement | Raw Sewage | Unknown |  | CUSTOMER CALLED MDC | LESS THAN 100 GAL | MDC PERSONEL | No |  | 2024-03-07 | 02:30 AM | 100-1000 GAL | 850 |  | M/S WAS REPAIRED IN THE STREET | Hartford | 38 Stonington St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Snowmelt | 2024-01-16 | 10:45 AM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident | <100g | MDC personnel | No |  | 2024-01-16 | 03:30 PM | <25g | 20 |  | MDC crews relieved & are repairing M/S | Hartford | 22 Center St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | M/S SURCHARGED | PASSER BY | <100G | MDC PERSONNEL | No |  | 2024-01-11 | 07:00 AM | 100-1000g | 850 |  | Levels receded | Hartford | 225 New Park Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | M/S BACKED UP | HOMEOWNER | <100G | MDC PERSONNEL | No |  | 2024-01-10 | 02:15 AM | <100G | 90 |  | JET TRUCK RELIEVED M/S | Hartford | 53 Arlington St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | M/S BACKED UP | HOMEOWNER | <100G | MDC PERSONNEL | No |  | 2024-01-10 | 02:15 AM | <100G | 90 |  | M/S RELIEVED BY JET TRUCK | Hartford | 49 Arlington St, Hartford, CT
[17 empty] | TOTAL VOLUME | 184599

## LITCHFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
LITCHFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-12-18 | 09:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots | We believe it was cause by a root ball within 10 feet of the manhole down stream from the SSO, and this manhole is less than 3 feet deep. The next manhole downstream was full, but no influent was seeping out of it, | A jogger saw it and called the treatment plant at 9:20 am. | 25 gallons per minute or up to 36,000 gallons per day. Since the downstream manhole was not over flowing, we think this blockage may have started with 24 hours or less, but can not be absolutely sure when it began. | Visuals observations. | Yes | It first reached a section of wetlands, which had water in it, around 75 feet from the river. Due to the volume we believe it was reaching the river, although the visual observation of the river, just down stream of this location did not display any disco | 2024-12-18 | 11:15 AM | We can not be entirely accurate, as we do not know how long this SSO has been happening for, but the very least amount would be 36,000 gpd. | 36000 |  | We were able to clear the blockage in about 20 minutes of jetting over 600 feet of sewer line. | Litchfield | 159 South St, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Dry | 2024-07-02 | 03:15 PM | Select... | Raw Sewage | Sewage Line Blockage - Rags | This section of our system is a 6" VCP, which was relined back in the 1970's and installed back in the 1930's. The manhole that overflowed was only 3.5 ft. deep. The blockage occurred more 500 ft. down stream about 20 ft. from this next manhole. | We were mowing this section of the sewer line right-a-way and it was discovered by the plant Superintendent. | 20-30 GPM. | Visual observations, a video was filmed too. | No |  | 2024-07-02 | 08:00 PM | We inspected upstream manholes and no others showed any issues with a over flow. One that was 500 ft. upstream di have a water mark 4" about the sewer pipe. This may indicate that the black started earlier that day , as the line never really surcharged. I | 43300 | 30 gpm x 1440=43,300 gallons. | We had to jet more than 500 ft. to resolve the issue. | Litchfield | 159 South St, Litchfield, CT
[17 empty] | TOTAL VOLUME | 79300

## MANCHESTER
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2024-12-12 | 08:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease in Sewer line caused back up | Homeowner called in | 1500 Gallons | Volume calculated by area/depth | No |  | 2024-12-12 | 08:30 PM | 1500 gallons | 1500 |  | Jetted sanitary sewer main | Manchester | 20 McKee St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2024-08-22 | 02:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots |  | Easement inspection by Water Dept. personnel | Less than 100 Gal | Visual estimation | No |  | 2024-08-22 | 02:15 AM | Less than 100gal | 90 |  | Cleared blockage with combination sewer truck, line is added to routine maintenance list for further review. Area cleaned up. | Manchester | 433 N Main St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2024-01-31 | 02:30 PM | Treatment Plant | Raw Sewage | Sewage Line Blockage - Grease | Air releifs in the line to releif air had grease in them | HI Alarm on Scada System | 4.4MGD flow estimated at the time | By flow at the time on the SCADA system | Yes | Hockanum River | 2024-01-31 | 04:30 PM | 200,000 max | 200000 |  | Pulling injection pump from a condensate manhole that was injecting air into the line. The air reliefs that are closest to the pump were bound with grease restricting air reliefs | Manchester | 311 Olcott St, Manchester, CT
[17 empty] | TOTAL VOLUME | 201590

## MANSFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Dry | 2024-11-19 | 04:45 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | line break on the force main | Reported to utilities department | >1000 | Visual inspection rough calculation of volume based on aera and depth | No |  | 2024-11-19 | 11:45 PM' | <1000 Gallons | 900 |  | Vac truck was called to manage lift station, pipe was excavated with backhoe as well as vacuum excavation truce, break was identified, and a repair coupling was used | Mansfield | 16 King Hill Rd, Mansfield, CT
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-01-10 | 01:45 AM | Pump Station | Raw Sewage | Excessive Flows - Snow Melt |  | Call came in from our 24-hr. monitoring center @ approx. 2:00am | Will not know until event is finished will update once flows subside.50000-75000 gallons | Pump/Pipe capacity 1000 GPMEstimate 225 GPM lost over full time of event.Full time of event will be updated after event is over.Event ended @ 6:30 am | No |  | 2024-01-10 | 06:30 AM | estimated to the high end of the by-pass @ 75000 gallons. | 75000 |  | Flows subsided resulting in the by-pass ending. | Mansfield | 30 Plains Rd, Mansfield, CT
[17 empty] | TOTAL VOLUME | 75900

## MERIDEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MERIDEN | Closed | Sewage Bypass | Dry | 2024-03-03 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | passer by | 750 gallons | visual observation | No | into storm catch basin system | 2024-03-03 | 10:15 AM | 750 gallons | 750 |  | flush main and vac out debris. clean out catch basins affected. light HTH application | Meriden | Lewis Ave, Meriden, CT
MERIDEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-01-10 | 02:30 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | notified by scada system | ongoing |  | Yes | quinnipiac river | 2024-01-10 | 09:00 AM | 0.54 MGD | 540000 |  |  | Meriden | 226 Evansville Ave, Meriden, CT
[17 empty] | TOTAL VOLUME | 540750

## MIDDLETOWN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MIDDLETOWN WPCA | Closed | Sewage Bypass | Dry | 2024-02-12 | 08:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots |  | Homeowner called it in. | 0-30 Gallons | by eye | No |  | 09/12/2024 | 07:00 AM | Less than 100 gallons | 90 | Spray mister flow rate and time | Misters shut off while repairs were in progress. | Middletown | 20 Kent Ct, Middletown, CT
[17 empty] | TOTAL VOLUME | 90

## MILFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MILFORD - BEAVERBROOK | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy flows, | Inspection of the plant processes. | No estimation, Loosing solids over final tank weirs. | no estimation is made. | Yes | Housatonic River | 2024-01-11 | 07:00:00 AM | 1.6 million gallons | 1600000 | Solids were overflows the weirs causing partial disinfection for half the day. I divided the days flow in half. | Storm flows went down | Milford | 75 Deerwood Ave, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2024-10-11 | 07:00 AM | Treatment Plant | Sludge Spill | Other | Human error | An operator making the morning rounds | 50-100 gallons | many years of experience. | No |  | 2024-10-11 | 09:00 AM | 50- 100 gallons | 85 |  | Raw sludge pump(s) was turned off immediately and locked out. McVac was called in and a septic truck already on site sucked up the sludge. Five plus operators squeegeed the sludge into the suction hoses. Two jet trucks washed down the area. | Milford | 1255 Oronoque Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2024-09-14 | 05:00 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Wastewater leaking from unused parallel force main. A plug is used to stop ww flowing from the active main into the unused main in the discharge manhole. Plug failed and was replaced. | Public Works Director | 200 gallons | estimated by estimating | No |  | 2024-09-14 | 06:30 PM | 200 | 200 |  | Reinflated plug in unused force main. Replacement plug has been ordered. | Milford | 404 West Ave, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2024-07-21 | 01:45 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Pump Failure | Resident called fire dept | 80 | DEEP representative | Yes | small stream not named/ possibly Oyster River | 2024-07-21 | 02:30 AM | 80 | 80 |  | Unclogged pumps, clean and CCTV sanitary main, repair road, we will be troubleshooting Watrous pump station to determine why alarm system failed to call out and repair. | Milford | 28 Brewster Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 10:30AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | by checking plant during the day | N/A | N/A | Yes | Housatonic | 2024-03-08 | 06:15 AM | 12MG | 12000000 | 3/7/24 = 15.5 MGD and 3/8/24 = 14.0 MGD. The event lasted from 3/7/24 @ 10:30 AM to 3/8/24 @ 6:15 AM. Averaging the flows and about 20 hours I come up with approximately 12 MGD. | Addition of Polymer and reduction of flow from storm | Milford | 1225 Oronoque Rd, Milford, CT
[17 empty] | TOTAL VOLUME | 13600365

## MONTVILLE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MONTVILLE | Closed | Sewage Bypass | Dry | 2024-09-20 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Break in sewer force for Holly Hill Pump Station. Not large surface release. | Normal Pump Station daily inspection (four main stations) showed sewer water on street (Route 32) at Holly Hill. Odors present. | 500 g | Estimated based on surface expression. | No | n/a (closest is Trading Cove Brook) | 2024-09-20 | 09:45 AM | 500 g | 500 |  | Repair band to force main after excavation to expose pipe. | Montville | 2517 Norwich-New London Turnpike, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2024-06-08 | 02:15 AM | Sewer Main | Partially Treated Raw Sewage | Sewage Line Break, Crack or Failure | New $3 million pipeline replacement project will be remedy to prevent from occurring in the future. Release in area of old (failing) pipeline. Line pressure due to pig shot through old line causing failure. | Police notification to dispatch then to WPCA on-call employee. Mayor notified. Health Director notified. WPCA Administrator, Chair/Assistant Chair all notified. Left message for adjacent homeowner. | 2,500 gallons | Responding on-call operator. Once observed, called operations room at industrial facility to stop discharge. | No | n/a | 2024-06-08 | 02:30 AM | 2500 gallons of paperboard wastewater. | 2500 |  | Responding on-call operator observed, called operations room at industrial facility to stop discharge. Vac truck cleaned up water. Lime spread for odor control. Adjacent homeowner notified. | Montville | 138 Maple Ave, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Rain greater than 4" per hour | 2024-03-27 | 06:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | hydraulic overload due to extreme weather conditions | visual inspection of the effluent | 0.1 mg | visual inspection and internal lab analysis | Yes | Thames River | 2024-03-29 | 06:00 AM | 2 mg | 2000000 |  | Rain ended. Polymer added to SBRs for coag / floc | Montville | 83 Pink Row, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2024-02-26 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Force Main break for Kitemaug Pump Station with flow at Kitemaug and Massepeag Roads | Routine Pump Station Inspection | 1,000 g | Visual inspection. | Yes | Tributary to Horton Cove at Kitemaug/Massepeag Roads | 2024-02-26 | 01:00 PM | 1,000 g of untreated wastewater from Force Main at Kitemaug Pump Station | 1000 |  | Discovery lead to bypass by pumper truck pumping out wetwell and emergency contractor repair of force main so online by 5 p.m. | Montville | 136 Massapeag Rd, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Rain greater than 4" per hour | 2024-02-21 | 06:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | hydraulic overload due to repeated extreme weather conditions | visual inspection of effluent/internal lab analysis | 0.1 | visual inspection | Yes | Thames River | 2024-02-29 | 06:00 AM | 1 mg | 1000000 |  | storm event ended. poly addition to SBRs. | Montville | 83 Pink Row, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Rain greater than 4" per hour | 2024-01-24 | 06:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | hydraulic overload due to significant repeated rain events | visual inspection of effluent/internal lab results | 0.1 mg | inspection of effluent | Yes | Thames River | 2024-01-31 | 06:00 AM | 2 mg | 2000000 |  | extreme rain event ended or subsided. poly addition to tanks for coag / floc | Montville | 83 Pink Row, Montville, CT
[17 empty] | TOTAL VOLUME | 5004000

## NAUGATUCK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain greater than 4" per hour | 2024-08-18 | 08:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Operator noticed overflow from manhole | 200-300 gpm | visual | Yes | Naugatuck River | 2024-08-19 | 12:00 PM | <200,000 gallons | 190000 |  | Flows subsided | Naugatuck | Cross St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2024-07-13 | 09:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Home owner noticed it in his back yard. | About 1500 gallons or 20 gallons a minute. | Visual estimation | Yes | Thurston Pond | 2024-07-13 | 10:30 PM | Around 1500 gallons | 1500 |  | The main sewer line was jetted. | Naugatuck | 63 Melbourne St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2024-06-27 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility |  | It was found during PM jetting. | About 10 gallons a min for 3 hours. Around 1800 gallons. | Visual estimate. | Yes | Long Meadow Pond Brook | 2024-06-27 | 12:00 PM | 1800 | 1800 |  | Sewer line was plugged and bypassed as the repair was made. | Naugatuck | 35 Elm St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-02-02 | 06:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Home owners discovered | 100 to 200 gallons | 1 to 2 inches of sewage on basement floor | No |  | 2024-02-02 | 08:00 AM | 100 to 200 gallons | 175 |  | High velocity jetting | Naugatuck | 4 Celentano Dr, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2024-01-22 | 08:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident from the neighborhood called the town. | 200 gallons | Visual estimation | No |  | 2024-01-22 | 10:45 AM | 200 gallons | 200 |  | The main line was jetted | Naugatuck | 5 Springdale Ave, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 06:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Employee was sent to m/h to check flow. | 20 gallons a min | Estimate by sight over the length of a min | Yes | Naugatuck River | 2024-01-10 | 10:00 AM | ~ 5,000 gallons | 5000 |  | flows from rain event started to subside | Beacon Falls | 1 Borgnis Rd, Beacon Falls, CT
[17 empty] | TOTAL VOLUME | 198675

## NEW CANAAN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW CANAAN STP | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-08-18 | 04:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Because of excessive flow we had to shut off UV and pull it out of the channel before it got to the electrical water was almost floor level | Operators were on site because of a storm with over 7inches of rain | Estimated 337,000 Gal of waste water we were back on line in 2 hours | The total flow for the storm was 4.4 million gallons divided that by 24 hours 183,000 an hour so for 2 hours would be 367,000 gal | Yes | 5 Mile River | 08/18/2024 | 06:00 PM | 367,000 gallons | 367000 | The total flow for the storm was 4.4 million gallons divided that by 24 hours 183,000 an hour so for 2 hours would be 367,000 gal | Flow receded to the point where we could begin U.V. disinfection again. | New Canaan | 394 Main St, New Canaan, CT
[17 empty] | TOTAL VOLUME | 367000

## NEW HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-12-30 | 04:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-12-30 | 07:30 AM | 2.9711 MG | 2971100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-12-18 | 08:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | New Haven Harbor | 2024-12-18 | 11:00 PM | 2.0975 | 2097500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-12-17 | 01:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-12-17 | 03:30 AM | 1.9813 MG | 1981300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-12-11 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-12-11 | 11:00 PM | 6.5983 MG | 6598300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-12-09 | 05:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | UNDETERMINED ON GOING | Yes | NEW HAVEN HARBOR | 2024-12-09 | 06:30 PM | 0.8251 MG Diverted | 825100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-11-28 | 10:30AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA | ONGOING | ONGIONG | Yes | NEWHAVEN HARBOR | 2024-11-28 | 04:00 PM | 7.7254 MG | 7725400 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-11-22 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-11-22 | 02:45 AM | 3.8851 MG | 3885100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-11-21 | 07:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-11-22 | 00:00 AM | 2.2733 MG | 2273300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-11-06 | 12:15 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | Contractor was setting up a by-pass pump for sewer lining project and had a cracked hose. The pump was tested and shut down. The sewage was contained and cleaned up by the crew with the vac truck. Crew estimated less than 50 gallons were spilled. All sewa | Contractor notified the GNHWPCA engineering dept. | Less than 50 gallons. | Field estimate by crew. | No | N/A | 2024-11-06 | 12:45 PM | Less than 50 gallons. | 45 |  | Contractor contained the spill and cleaned it with a vac truck. The effected area was washed down and all sewage was removed. | New Haven | 131 -33 Canner St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-10-07 | 08:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | SCADA | Yes | NEW HAVEN HARBOR | 2024-10-07 | 10:45 AM | 2.19 MGD | 2190000 |  | Event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-10-02 | 04:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Debris in line, possible broken pipe. Broke pipe caused backup. | Called in by RWA | Less than 500 gallons | Field estimate | No |  | 2024-10-02 | 06:30 PM | Less than 500 gallons | 450 |  | Ongoing at this time. Line was jetted and partial flow restored. The line has issues that will be repaired 10/3/2024. The bypass has stopped at this time.Pipe was cleared and flow restored. The pipe was repaired 10/3/2024 by Laydon Construction. | New Haven | 320 Fitch St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-09-27 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-09-27 | 02:30 AM | 2.8683 MG | 2868300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-09-07 | 06:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ongoing | ongoing | Yes | New Haven harbor | 2024-09-07 | 08:30 PM | 2.5815 MG | 2581500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-26 | 00:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-08-26 | 03:00 AM | 3.2158 MG | 3215800 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-19 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 8.389 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2024-08-19 | 07:45 AM | 8.389 MGD | 8389000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-08-18 | 04:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 7.512 MGD | SCADA flow monitoring | Yes | NEW HAVEN HARBOR | 2024-08-18 | 09:45 PM | 7.512 MGD | 7512000 |  | Rain subsided | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-08-06 | 02:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2024-08-06 | 11:45 PM' | 5.8046 MG | 5804600 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-08-04 | 06:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-08-04 | 08:00 PM | 1.3983 MG | 1398300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-03 | 05:45 PM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Stormflow | SCADA Flow monitoring | 4.1596 MG | SCADA Flow monitoring | Yes | New Haven Harbor | 2024-08-03 | 08:30 PM | 4.1596 MG | 4159600 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-29 | 07:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2024-07-29 | 08:45 AM | 1.0227 MG | 1022700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-07-23 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-07-23 | 02:30 AM | 0.3395 MG | 339500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-07-18 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 2.529 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2024-07-18 | 02:15 AM | 2.529 | 2529000 |  | Rain ebded | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-17 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-07-18 | 00:00 AM | 0.8333 MG | 833300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-13 | 08:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor. | 2024-07-13 | 01:30 PM | 6.5602 MG | 6560200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-06 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-07-06 | 01:00 PM | 4.2583 MG Diverted | 4258300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-07-05 | 10:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-07-06 | 00:00 AM | 1.2232 MG | 1223200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-06-30 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-06-30 | 06:30 PM | 2.9327 MG | 2932700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-06-28 | 05:45 PM | Treatment Plant | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor dumped his truck too fast and overwhelmed the septuagenarian receiving facility. The waste ran out of the pit and into the street. | Operator on shift witnessed the spill. | Less then 500 gallons. | Field estimate by crew. | No | N/A | 2024-06-27 | 06:00 PM | Field estimate by crew. | 450 |  | GNHWPCA Collections personnel cleaned the spill after the contractor refused to respond. | New Haven | 45 Connecticut Ave, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-06-27 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-06-27 | 05:15 AM | 1.9437 MG | 1943700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-06-26 | 10:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | New Haven Harbor | 2024-06-26 | 10:45 PM | 1.2102 MG | 1210200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-06-22 | 06:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor. | 2024-06-22 | 09:00 PM | 3.3128 MG Diverted | 3312800 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-06-21 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-06-21 | 10:00 PM | 4.2131 MG Diverted | 4213100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-06-06 | 05:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-06-06 | 06:30 AM | 1.1984 MG | 1198400 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-05-30 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-30 | 07:45 AM | 1.2225 MG | 1222500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-05-27 | 11:30 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | SCADA Flow monitoring | ONGOING | ONGOING | Yes | New Haven Harbor | 2024-05-27 | 09:45 PM | 3.2729 MG | 3272900 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2024-05-23 | 11:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-23 | 02:30 PM | 3.2382 MG | 3238200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-05-16 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-16 | 04:45 AM | 5.3887 MG | 5388700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-05-15 | 12:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-16 | 00:00 AM | 1.1537 MG | 1153700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-05-10 | 04:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-10 | 07:15 AM | 1.0269 MG | 1026900 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2024-05-08 | 08:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-08 | 11:00 AM | 3.5179 MG | 3517900 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-05-06 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-06 | 01:00 AM | 0.4431 MG | 443100 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-05-05 | 11:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-05-06 | 00:00 AM | 0.3643 MG | 364300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-04-25 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | The line had grit in it, possible grease and rags. | Drain cleaning contractor working on the property reported it. | 500 gallons were discharged to the basement floor. | 1.5"x16'x30'x7.48=488.8 gallons | No | N/A | 2024-04-25 | 01:45 PM | 500 Gallons | 500 |  | Crew jetted the city line and restored flow. Pro Klean was contracted to clean and sanitize the basement. | New Haven | 147 Henry St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-18 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-04-18 | 05:00 AM | 0.9494 MG | 949400 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-17 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-04-18 | 00:00 AM | 0.1297 MG | 129700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-12 | 02:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-04-12 | 07:00 AM | 4.6012 MG Diverted | 4601200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-11 | 08:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-04-12 | 00:00 AM | 1.7857 MG | 1785700 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-04-04 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-04-04 | 05:30 PM | 8.5826 MG | 8582600 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-03 | 08:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | New Haven Harbor. | 2024-04-04 | 00:00 AM | 13.620 MG Diverted | 13620000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-04-02 | 03:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | New Haven Harbor | 2024-04-03 | 00:00 AM | 0.4826 MG Diverted | 482600 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-28 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-29 | 00:00 AM | 9.8187 | 9878700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-03-25 | 12:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Crew jetted the line in front of the school bus yard to break the line free. The line was blocked with grease. | Resident called it in. | 50 gallons of sewage. Sewage bubbled through the pick holes in the MH cover. | Field estimate by crew. | No | N/A | 2024-03-25 | 01:15 PM | Crew estimated less than 50 gallons were discharged from the manhole cover. | 45 |  | Crew jetted the line and restored flow. | New Haven | Bella Vista Dr, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-03-24 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-24 | 03:00 PM | 0.4569 MG | 456900 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-23 | 08:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | New Haven Harbor | 2024-03-24 | 00:00 AM | 19.775 MG | 19775000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-03-11 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-11 | 11:30 AM | 1.681 MG | 1681000 |  | Return to normal flow | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-10 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-11 | 00:00 AM | 22.605 MG | 22605000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-09 | 06:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-10 | 00:00 AM | 4.840 MG | 4840000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-07 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-07 | 11:00 PM | 16.710 MG | 16710000 |  | rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-03-06 | 04:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-07 | 00:00 AM | 8.8212 MG | 8821200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-05 | 10:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA |  | SCADA Flow monitoring | Yes | New Haven Harbor | 2024-03-05 | 07:30 PM | 1.4244 MG | 1424400 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-03 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-03-03 | 00:15 AM | 0.027 MG | 27000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-03-02 | 02:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 1.0 in Rain | SCADA |  |  | Yes | New Haven Harbor | 2024-03-03 | 00:00 AM | 11.295 MG | 11295000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-02-28 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 0.6 in Rain | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-02-28 | 01:00 AM | 0.74 MG | 740000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-02-27 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain Event | SCADA |  |  | Yes | NEW HAVEN HARBOR | 2024-02-28 | 00:00 AM | 2.99MG | 2990000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-02-26 | 09:30 PM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | Force main break. Cast iron pipe had a crack. | New Haven Police called it in. | Less than 50 gallons | Field estimate by crew. | No | N/A | 2024-02-27 | 11:00 AM | Less than 50 gallons. | 45 |  | This is ongoing at this time. Brennan Construction repaired the force main, and the pump station is back on line. There was less than 50 gallons discharged. The crew set up booms to stop any sewage and a vac truck removed the sewage. | New Haven | 5 Pope St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2024-02-05 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Line was blocked with grease and rags. The line was cleared at the intersection of Hillcrest and Dixwell. | Property owner called it in. | Less than 100 gallons at the time of inspection. | Field estimate by crew. | No | N/A | 2024-02-05 | 01:30 PM | Less than 100 gallons. | 85 |  | Crew jetted the line at the intersection of Hillcrest and Dixwell Ave. The line broke free and drained. The line was full of grease. The property owner removed a clean out cap and the water in the basement drained out. | New Haven | 1676 Dixwell Ave, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-01-28 | 06:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 11.143 Mgd | SCADA | Yes | NEW HAVEN HARBOR | 2024-01-28 | 09:00 PM | 11.143 MGD | 11143000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-24 | 09:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 0.1 in. Rain | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2024-01-24 | 11:45 PM' | 0.7025 MG | 702500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-14 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Previous days rain event | SCADA | 0.2479 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2024-01-14 | 05:00 AM | 0.2479 Mgd | 247900 |  | Rain event | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-13 | 02:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 18.53 MGD | SCADA | Yes | New Haven Harbor. | 2024-01-13 | 11:45 PM' | 18.53 Mgd | 18530000 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2024-01-11 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Previous days rain event | SCADA | 0.0923 Mgd | SCADA | Yes | NEW HAVEN HARBOR | 2024-01-11 | 00:15 AM | 0.0923 MGD | 92300 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2024-01-10 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 17.919 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2024-01-10 | 11:45 PM' | 17.919 Mgd | 17919000 |  | Carried over to next day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2024-01-09 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA | SCADA | SCADA | Yes | NEW HAVEN HARBOR | 2024-01-09 | 11:45 PM' | 8.116 MGD | 8116000 |  | Day ended, event carried over to next day | New Haven | 345 E Shore Pkwy, New Haven, CT
[17 empty] | TOTAL VOLUME | 305829220

## NEW LONDON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2024-12-12 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor hit 16" force main fed from Pump Station 5 on Thomas Griffin Road New London CT. Crews on route to isolate and repair | Called in to our customer service department by the contractor who hit it during excavation. | 150,000 | By using flow trends | Yes | Thames river | 2024-12-13 | 05:00 AM | 149,000 gallons reached the Thames River and 1,260,000 gallons were collected by septage trucks, preventing it from reaching the water body. | 149000 |  | Veolia crews removed the broken section of piping and replaced with new. | New London | 140 Ferry St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2024-01-13 | 08:45 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Due to incoming flows from heavy rains our clarifiers started to bulk over and made it into the effluent. | Operators monitoring the plant due to recent heavy flows. | N/A | N/A | Yes | Thames River | 2024-01-14 | 01:30 AM | Unable to determine | 1000 |  | Flows came down, helping to give our clarifiers more settling time. | New London | 100 Trumbull St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 08:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | With the storm last night into this morning the flow increase caused a surcharge in the gravity line the bypass discharges into. Also due to surcharging of gravity main there were some homes and basements affected by the bypass. The drop down selection on | Field Service Crews and STP Ops performing storm coverage | Unable to determine. Our pump station flow meter was unable to be integrated into the bypass line. | N/A | Yes | Thames River. Multiple sections located near Pequot Avenue NLCT | 2024-01-11 | 10:30 PM | Due to bypassing main discharge line of Pump Station 1 there is no flow measurement. | 5000 |  | Crews ran almost 2000 or so feet of temporary bypass line directly to Pump Station 2 in order to stop surcharging the gravity system. | New London | Neptune Ave, New London, CT
[17 empty] | TOTAL VOLUME | 155000
THESE BYPASSES WERE REPORTED DUE TO HIGH FLOW AT THE PLANT BUT DID NOT RESULT IN SOLIDS LEAVING THE PLANT AND ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
NEW LONDON STP | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 01:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | high flow rates due to rainfall amount | Operators performing storm response procedures | N/A | N/A | Yes | Thames River | 2024-03-07 | 07:30 AM | N/A | 0 |  | Flows lessened allowing our clarifier blankets to begin settling again. | New London | 100 Trumbull St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 03:45 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | During the storm event overnight we started to bulk out of our clarifers and it made it into the effluent. Due to high flows were are still bulking at the time of this report. | Operators on storm coverage. | N/A | N/A | Yes | Thames River | 2024-01-11 | 00:30 AM | N/A | 0 |  | Elevated flows from rainstorm came down. | New London | 100 Trumbull St, New London, CT
THIS BYPASS WERE REPORTED BUT HAD NO FLOW
They are included here to show that they were reported in good faith.
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2024-01-01 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | An off duty STP operator found a puddle of water near our force main that recently had broken twice and immediately called our field service crews. | N/A | N/A | No |  | 2024-01-01 | 05:45 PM | N/A | 0 |  | We switched over to our temporary bypass line that we recently installed. | New London | Pequot Ave, New London, CT

## NEWINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-19 | 08:00 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | PLANNED BY-PASS | MDC PUMP STATION CREW | <1000G | MDC PUMP STATION CREW | Yes | WEBSTER BROOK | 2024-08-20 | 03:15 AM | 183,120 Gallons | 183120 |  | Once flow lowered | Newington | 98 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 07:45 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | PLANNED BY-PASS | MDC PUMP STATION CREW | <100G | MDC PUMP STATION CREW | Yes | WEBSTER BROOK | 2024-08-19 | 07:00 AM | 287,750 Gallons | 287750 |  | Rain event ended | Newington | 98 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-03-10 | 08:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Main Sewer Surcharged | Homeowner | <100G | MDC Personnel | No |  | 2024-03-11 | 03:00 PM | <100G | 90 |  | LEVELS RECEDED | Newington | 56 Clifford St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-07 | 01:00 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 100 GAL | MDC PERSONEL | Yes | WEBSTER BROOK | 2024-03-07 | 12:15 PM | 283,800g | 283800 |  | Levels receded | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 11:45 PM' | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 100 GAL | MDC PERSONEL | Yes | MILL BROOK | 2024-03-07 | 11:30 PM | 1000-25000g | 20000 |  | Levels receded | Newington | 175 Cedar St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 04:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | SURCHARGE RAIN EVENT | HOMEOWNER | <100G | MDC PERSONNEL | No |  | 2024-01-11 | 07:00 AM | <100g | 90 |  | Levels receded | Newington | 54 8th St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:45 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Bypass due to wet weather event | MDC personnel | <1000g | MDC personnel | Yes | WEBSTER BROOK | 2024-01-10 | 07:00 PM | 777,000G | 777000 |  | Levels receded | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 09:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | TOWN OF NEWINGTON | <1000g | MDC PERSONNEL | Yes | MILLBROOK | 2024-01-11 | 07:00 AM | 100-1000g | 850 |  | Levels receded | Newington | 175 Cedar St, Newington, CT
[17 empty] | TOTAL VOLUME | 1552700

## NORTH HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORTH HAVEN WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-12-18 | 10:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | The sewer main backed up due to roots which caused rags to build up. Roots protruding through the pipe joint. | Resident called the north haven police, who relayed the information to Veolia emergency staff. | Less than 15 gallons | Visual observation. | No |  | 2024-12-18 | 11:30 PM | less than 15 gallons | 13 |  | As noted above, staff cleared the sewer blockage. We also added this location to the 90 day hot spot cleaning list. Additionally, we will have this location treated for roots, and ultimately lines to prevent root intrusion. | North Haven | 46 Marlborough Rd, North Haven, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2024-05-11 | 00:00 AM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | LEAK AT LOW PRESSURE SEWER SYSTEM CURB BOX, ALTHOUGH THE LINE WAS NOT ACTIVE, THE PIPE STUB THAT WAS CAPPED WAS STILL PART OF THE ACTIVE PIPING SYSTEM. | RESIDENT WAS MOWING HIS LAWN | 5-10 GALLONS ESTIMATED INITIALLY, NEW ESTIMATE IS 25-50 GALLONS FOR THE EVENT DURATION. WE PUMPED THE POOLED SEWAGE INTO THE GRAVITY MAIN | VISUAL ESTIMATE | No |  | 2024-05-15 | 03:45 PM | 25-50 GALLONS | 40 |  | EXCAVATION AND PVC PIPE REPAIR | North Haven | 139 Summer Ln, North Haven, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2024-04-26 | 12:00 PM | Treatment Plant | Raw Sewage | Other | AN OPERATOR MISTAKENLY DID NOT OPEN THE CORRECT VALVE TO FILL THE TRUCK WHICH CAUSED ROUGHLY 750 GALLONS TO SPILL ONTO THE GROUND IN THE SEPTAGE LOADING AREA | OPERATOR NOTICED IT AFTER TURNING ON THE PUMP | ESTIMATED 500-750 GALLONS OF 6% SOLIDS SLUDGE | VISUAL OBSERVATION | No |  | 2024-04-26 | 02:00 PM | ESTIMATED 750 GALLONS | 750 |  | STAFF PICKED UP THE SPILLED SLUDGE WITH SHOVELS, SQUEEGEES AND A SKID STEER LOADER DUE TO THE SLUDGE THICKNESS. | North Haven | 1122 Universal Dr N, North Haven, CT
[17 empty] | TOTAL VOLUME | 803

## NORWALK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-08-07 | 07:15 AM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | The Secondary Scum pump stopped working properly due loss of pressure. | Operator making rounds. | 200-300 gallons | Vactor Truck | No |  | 2024-08-07 | 08:00 AM | 200-300 gallons | 250 |  | On site team cleaned up spill and fixed equipment that malfunctioned. | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-03-06 | 11:45 AM' | Treatment Plant | Partially Treated Raw Sewage | Other | The Vactor water tank was overfilled, and spilled plant effluent water into the parking area. | An employee saw truck overflowing | <500 gallons | Visual inspection. | No |  | 2024-03-06 | 11:45 AM' | <500 gallons | 450 |  |  | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-12-20 | 07:15 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | The force main on Howard Ave had a beam break due to differential settlement | Public works | Less than 100 gallons | Vactor Truck | No |  | 2024-12-20 | 11:15AM | less than 100 gallons | 90 | Vactor Truck | Repair was made to sewer break | Norwalk | 60 Howard Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 05:45 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | An extreme storm event causing a catastrophic failure to all equipment in the pump station. The station is located adjacent to Keeler Brook, during the storm event, stormwater entered and filled the drywell side of the Keeler Brook Pump Station | SCADA System indicated Pump Station Loss of Communication. Dispatched maintenance crew to investigate the loss of communication. | 1.4 to 1.8 million gallons | Based on average pump station flow and duration of SSO/ bypass. | Yes | Keeler Brook | 2024-08-19 | 03:15 AM | 1.4 to 1.8 million gallons | 1700000 |  | The Keeler Brook Pump Station is currently operating on a temporary bypass using Godwin pumps that are connected into the existing collection system force main. | Norwalk | 473 Connecticut Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-07-12 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Norwalk police dept called Norwalk WPCA | 500-1000 gallons | Vactor Truck | Yes | Saugatuck River | 2024-07-13 | 02:30 AM | About 800 gallons | 800 |  | Contractor repaired force main break. | Norwalk | 56 County St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-04-28 | 05:30 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Complete pump failure at station. | A city resident reported the SSO. | 34,362 gallons. | SCADA historian and critical wet-well level knowledge. | Yes | Indian River | 2024-04-28 | 07:30 PM | 34,362 gallons. | 34362 |  | Repaired the equipment failure | Norwalk | 11 Leann Dr, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-03-22 | 11:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Force Main break | Routine pump station inspection. | <1000 gallons | Visual inspection and amount recovered in vac truck | No |  | 2024-03-22 | 04:00 PM | Unknow | 800 |  | The force main leak was repaired. | Norwalk | 33 S Beach Dr, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-07 | 06:30 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Bypass pumps operated by construction contractor ran out of fuel. | Pump Station inspection | <2500 gallons | Visual inspection and amount recovered in vac-truck. | Yes | Wilson Cove | 2024-03-07 | 06:30 AM | <2500 gallons | 2500 |  | See comments above. | Norwalk | Old Trolley Way, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-01-15 | 07:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure |  | Crew called in SCADA hi wet well Keeler Brook Pump Station. | Unknown at this time | Unknown at this time | Yes | Keeler Brook | 2024-01-15 | 08:30 AM | Less than 500 gallons. | 450 |  |  | Norwalk | 473 Connecticut Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2024-01-11 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Resident called the Norwalk Customer Service | less than 100 gallons | Amount recovered in Vac truck | No |  | 2024-01-11 | 01:30 PM | Less than 100 gallons | 80 |  |  | Norwalk | 60 Connecticut Ave, Norwalk, CT
[17 empty] | TOTAL VOLUME | 1739782

## NORWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2024-07-26 | 10:30AM | Treatment Plant | Partially Treated Raw Sewage | Sewage Line Break, Crack or Failure | Final effluent from clarifier pipe to Chlorine contact chamber leaking into dewatering hole for plant construction. | Flow into hole dug for construction | 5,000 gallons | volume of construction hole effluent went into | No |  | 2024-07-26 | 01:00 PM | 5,000 | 5000 |  | Air filled plug was put into line, and we will dig and repair on Monday. Clarifier taken out of service. Low flow process control decision. | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2024-07-17 | 12:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Cracked FM | Customer Call | 100gpm | Visual Estimate | Yes | Thames River | 2024-07-18 | 02:00 AM | 882387 | 882387 |  | replaced 19 ft of FM | Norwich | 74 W Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2024-03-11 | 08:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Customer Call | 1-2 GPM | Visual estimate | No |  | 2024-03-11 | 09:00 AM | 100 Gallons | 100 |  | Jetted sewer main, cleared debris. | Norwich | 10 Laurel Hill Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2024-03-08 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Connection on FM broke | Customer Call | 5 GPM | Visual Estimate-Flow meter | Yes | Shetucket | 2024-03-08 | 12:30 PM | 42929 | 42929 |  | Repaired sewer service on FM | Norwich | 1 American Wharf Rd, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Customer Call | 5 GPM | Visual Estimate | Yes | Shetucket river | 2024-03-06 | 03:15 PM | 10,000 | 10000 |  | Jetted grease blockage | Norwich | 84 Hamilton Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-25 | 07:30 AM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Temporary bypass pipe had a hole in it. Replaced with 2 new sections. | Site walk | 10 GPM | Visual estimate | Yes | Shetucket | 2024-01-25 | 11:00 AM | 210724. | 210724 |  | Replaced pipe with two new pipes. | Norwich | 10 Laurel Hill Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-16 | 08:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Phone call from school janitor. | 500 gallons | Visual Estimate | No |  | 2024-01-16 | 09:15 AM | 500 Gallons | 500 |  | Jetted main | Norwich | 68 Thermos Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-16 | 10:15 AM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Vent for bypass came unlatched | Phone call | 500 GPM when station turns on. | Visual Estimate | Yes | Thames River | 2024-01-16 | 11:00 AM | 2500 | 2500 |  | Installed Vent pipe | Norwich | 1 W Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-01-12 | 05:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | CSO Email | 3919870 | Flow meter | Yes | Thames River | 2024-01-12 | 05:30 PM | 3919870 | 3919870 |  | Jetted main | Norwich | 3 Crown St, Norwich, CT
[17 empty] | TOTAL VOLUME | 5074010

## ORANGE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ORANGE | Closed | Sewage Bypass | Dry | 2024-02-21 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor hit the 2 inch pump station force main. Less than 20 gallons of sewage came up from the break. We did have a Call before you dig for this but no visible markings shown despite having a completed record. | The contractor who was digging to install a new water main discovered the break. | < 20 gallons | visual observation, estimated | No |  | 02/21/2024 | 11:00 AM | LESS THAN 20 GALLONS | 20 | VISUAL ESTIMATE | THE CONTRACTOR REPAIRED THE 2" FORCE MAIN. THE SMALL PUMP STATION WAS USED AS A HOLDING TANK WHILE THE PVC PIPE WAS REPAIRED . | Orange | Smith Farm Rd, Orange, CT
[17 empty] | TOTAL VOLUME | 20

## OXFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
OXFORD | Closed | Sewage Bypass | Dry | 2024-03-20 | 04:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Break in 10" Force Main | Contractor notified he found sewage water bubbling from the ground @ 7:45am. | 20,000 | 4 hrs @ 5,000 per hr | Yes | Little River | 2024-03-20 | 12:00 PM | 40,000 | 40000 |  | Repaired force main with new pipe | Oxford | 46 Towner Ln, Oxford, CT
[17 empty] | TOTAL VOLUME | 40000

## PLAINFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2024-06-20 | 08:00 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Broken orangeburg pipe. | Contractor on site doing preliminary work for lift station upgrade. | 500 Gallons | Estimate | No |  | 2024-06-20 | 05:30 PM | Less than 500 gallons, majority was able to be pumped to wet well and vac truck. | 450 |  | Excavated and replaced 8 inch SDR. | Plainfield | 55 Lathrop Rd, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2024-03-20 | 03:30 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Electrical/control issue. | Mechanic performing daily morning checks. | Approximately 1000 gallons | Received pump flow information from the downstream pump station from 03:00 and 06:00 hrs. and averaged it out. There is approximately 2 miles of sewer main to surcharge before releasing at the pumpstation manhole, so 1000 gallons is a high estimate. | Yes | Moosup River | 2024-03-20 | 07:45 AM | Approximately 1000 gallons | 1000 |  | Found loose electrical connections and a relay going bad. Went through all control panels and electrical buckets and tightened every wire and screw in the system. Cleaned contacts and replaced relay. Simulated and tested several times as well as tested | Plainfield | 337 N Main St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2024-07-02 | 01:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Pump Failure | Town police notified on-call personnel | 300 gallons | estimate | Yes | Moosup River | 2024-07-02 | 03:00 AM | 300 Gal. | 300 |  | removing rags from pumps | Plainfield | 376 N Main St, Plainfield, CT
[17 empty] | TOTAL VOLUME | 1750

## PLYMOUTH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2024-11-06 | 02:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Workers were GPS manholes in Sewer ROW's | Unknown - Very low flow area | Unknown | No |  | 2024-11-07 | 12:00 PM | 100 gallons | 100 |  | Line was jetted | Plymouth | 28 Lassy Ct, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2024-08-26 | 10:30AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | pin hole leak on top of pipe | called in | 0.25 gpm | small trickle on road | No |  | 2024-08-26 | 04:00 PM | less than 200 | 175 |  | Draining Force Main. Force Main was scheduled to be lined on 8/27/24. Lining is almost complete | Plymouth | 221 South St, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2024-03-07 | 02:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Removed some grease deposits after blockage was cleared | called in to Dispatch | 20gpm. Duration of discharge unknown. Blockage was cleared with 45 minutes after reported | unknown | Yes | Middle Pond | 2024-03-07 | 03:00 PM | 1000 + gallons | 1000 |  | Blockage was cleared with jet truck | Plymouth | 28 Holt St, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2024-02-05 | 10:15 AM | Select... | Raw Sewage | Sewage Line Break, Crack or Failure | Pin Hole leak on top of Force Main | WPCA personnel | 2 gpm | estimated | No |  | 2024-02-05 | 02:45 PM | 600 gallons | 600 |  | Drained down force main past leak, excavated area, CCTV pipe and replaced section of pipe | Plymouth | 221 South St, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2024-01-04 | 02:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Believe cause is from gas trapped in upper portion of force main pipe | Odor complaint called in to WPCA | 750 to 1000 gallons | 2gpm for approximately 6 hours | No |  | 2024-01-04 | 08:00 AM | 750 to 1000 gallons. | 850 |  | Contractor hired to replace section of pipe and vac truck hired to empty force main and keep up with incoming flow to pump station. | Plymouth | 211 South St, Plymouth, CT
[17 empty] | TOTAL VOLUME | 2725

## RIDGEFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2024-11-14 | 01:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Blockage in was caused by grease blockage in the line. | Called by building owner. | <75 gallons | Visual estimate and duration. | No |  | 2024-11-14 | 02:00 PM | <75 gallons | 70 |  | Cleared line with Vactor truck. | Ridgefield | 30 Bailey Ave, Ridgefield, CT
[17 empty] | TOTAL VOLUME | 70
|  | 8785 | Delete

## SEYMOUR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SEYMOUR WPCF, TOWN OF | Closed | Sewage Bypass | Rain greater than 4" per hour | 2024-08-19 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | River surged to biblical proportions, and washed out soil around infrastructure. | At 4:45 pm, staff discovered the overflowing manhole. | 5-10 gpm, still ongoing. | Visual observation. | Yes | Naugatuck River | 08/22/2024 | 12:45 PM | Since it was an estimated volume it was between 13650 and 27300 gallons. (5gpm - 10 gpm) | 20475 | Calculation | 1. By repairing the section of sewer line that was damage due to the line damage by washout water from the river during the storm | Seymour | 100 Bank St, Seymour, CT
[17 empty] | TOTAL VOLUME | 20475

## SHELTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SHELTON | Closed | Sewage Bypass | Dry | 2024-11-29 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident observed water in road and notified Sewer department. | 200 gallons | Visual | No |  | 2024-11-29 | 05:30 PM | 200 gallons | 200 |  | Vac truck vacuumed 3 catch basins and road.Broken pipe replaced. | Shelton | 20 Wakelee Ave, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2024-10-12 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | plus some grease, debris | Police observed manhole and called for Sewer assistance. | Less than 50 gallons | Visual | No | N/A | 2024-10-12 | 02:00 PM | less than 50 | 45 |  | jetted out main; removed rags, grease, debris | Shelton | 739 Long Hill Ave, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2024-07-22 | 09:00 PM | Basement | Partially Treated Raw Sewage | Sewage Line Blockage - Other | rags and grease in main line | Resident called. | 50 gallons | Visual | No | N/A | 2024-07-23 | 07:00 AM | 10 gallons | 10 |  | Main line jetted. Rags, grease removed.Cleaning service brought in for basement. | Shelton | 116-118 Maltby St, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2024-07-19 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | grease, rags | Resident called for assistance regarding smell. | 5 - 10 gallons | visual (spillage from manhole to edge of woods) | No | N/A | 2024-07-19 | 02:30 AM | 5 - 10 gallons | 8 |  | jetted out main; removed grease, rags | Shelton | 17 Coram Rd, Shelton, CT
[17 empty] | TOTAL VOLUME | 263

## SIMSBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SIMSBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-06-21 | 04:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Reported by Resident | Less than 20 Gallons | Visual determination | Yes | Farmington River | 2024-06-21 | 07:30 PM | Less than 20 gallons | 15 |  | flushing sewer line | Simsbury | 41 Main St, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-10 | 06:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | High flows due to rain event and snow melt, loss of solids from secondary clarifier. Effluent TSS on 1/11 was 233. | Operator morning inspection | total daily flow was 4.98 MGD | Effluent flow meter | Yes | Farmington River | 2024-01-11 | 07:00 AM | 4.98 MGD | 4980000 |  | Adjusted process flows for wasting and return sludge to minimize loss of solids. | Simsbury | 36 Drake Hill Rd, Simsbury, CT
[17 empty] | TOTAL VOLUME | 4980015

## SOUTH WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2024-08-27 | 04:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | UV disinfection shut down because of a communication failure | Through a SCADA alarm | 11,110 gallons | Approxiamte flow at the time was 1.6 mgd. 1,600,000/24/60*10. | Yes | Connecticut River | 2024-08-27 | 04:30 AM | 11,100 gallons | 11100 |  | Cleared previous communication alarm and communication came back | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2024-08-11 | 10:30AM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure |  | SCADA alarm stating UV lost power. UV was running within 5 minutes of receiving alarm | About 9,000 gallons | Effluent flow meter | Yes | Connecticut River | 2024-08-11 | 10:30AM | Approx 9,000 gallons | 9000 |  | Power transferred to commercial power | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2024-04-19 | 08:45 AM | Treatment Plant | Partially Treated Raw Sewage | Other | Equipment was accidentally taken off line | Lab analyst found filtrate coming out of filtrate station | About 4000 gallons | Gravity belt thickener flow meter. | No |  | 2024-04-19 | 09:15 AM | About 4000 gallons | 4000 |  | Stopped gravity belt thickener until Motor Control Center could be powered back up | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2024-01-22 | 11:45 AM' | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Resident called Monday morning to report overflow. | 90 | Vent hole method | Yes | Avery's Brook | 2024-01-22 | 12:00 PM | 90 gallons | 90 | By estimating how much had discharged from the manhole vent | Blockage was cleared | South Windsor | 171 Beelzebub Rd, South Windsor, CT
[17 empty] | TOTAL VOLUME | 24190

## SOUTHBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2024-10-31 | 09:15 AM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Roots | Found wipes and roots on the snake used for clearing the blockage. | Backed up into resident's condo unit. | 5 to 10 gallons total. | Estimated. | No |  | 2024-10-31 | 12:30 PM | 5 to 10 gallons. | 10 |  | Replaced 5 to 6 ft of 4" lateral. On Friday November 1st. | Southbury | 1040 Village St, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2024-09-30 | 11:00 AM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | Parking area was recently repaved. It is possible that it was broken by heavy equipment during construction. | A resident reported it. | 100 gallons per day. | Estimated 100 gallons per day. Some flow was still going through lateral. | No |  | 2024-10-01 | 01:00 PM | Probably less than 100 gallons. | 100 |  | Excavation of driveway and repaired the line. | Southbury | 668 A N Durkee Hill Ln, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Flash flood event. | Customer | Estimated 14,000 gallons discharged. | Visual estimate | Yes | Pomperaug river | 2024-08-19 | 01:00 PM | 14,000 gallons. | 14000 |  | An outside construction company replaced 8" main.And installed supports. | Southbury | 293 Krueger Cir, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Flash flooding caused embankment to wash away, exposing and breaking sewer main. | Member of the public called to report the damage to the system. | Approximately 14,000 gallons were discharged over 19 hours. | Estimated flow over estimated duration | Yes | Pomperaug River | 2024-08-19 | 01:00 PM | 14,000 Gallons | 14000 |  | Emergency replacement of existing sewer main | Southbury | 293 Krueger Cir, Southbury, CT
[17 empty] | TOTAL VOLUME | 28110

## SOUTHINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2024-06-24 | 07:15 AM | Pump Station | Raw Sewage | Electrical Equipment Failure |  | Town Of Southington WPC staff noticed water coming out of the manhole access hatch for the wet well. | 500 gallons | Estimate | No |  | 2024-06-24 | 08:00 AM | 500 gallons | 500 |  | Plant staff put the pump station in float mode until the electronics could be repaired. | Southington | 2156 West St, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2024-03-14 | 05:15 PM | Manhole | Raw Sewage | Other | Restaurant's Grease Trap | Southington Police Department called Southington WPC and notified them of water coming out of a manhole in a restaurant's parking lot. | 30 gallons | Estimate | No |  | 2024-03-14 | 06:00 PM | Estimate | 30 |  | Restaurant owner called a plumber. | Southington | 1763 Meriden-Waterbury Turnpike, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-13 | 01:15 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Excessive flows caused an alarm that notified plant staff. | 500,000 Gallons | Flow meter | Yes | Quinnipiac River | 2024-01-13 | 05:30 PM | 500,000 | 500000 |  | Plant staff closed the Denitrification Building's bypass valve when the plant's flows had stabilized. | Southington | 999 Meriden-Waterbury Turnpike, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 06:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Excessive flows caused an alarm that notified plant staff. | 6.997 Million Gallons | Flow meter | Yes | Quinnipiac River | 2024-01-11 | 04:15 PM | 6.997 Million Gallons | 6997000 |  | Plant staff periodically opened and closed the Denitrification Building's bypass valve as needed. Plant staff permanently closed the bypass valve when the plant's flow had stabilized. | Southington | 999 Meriden-Waterbury Turnpike, Southington, CT
[17 empty] | TOTAL VOLUME | 7497530

## STAFFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
[17 empty] | TOTAL VOLUME | 0
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY'S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
STAFFORD | Closed | Sewage Bypass | Dry | 2024-07-25 | 06:00 PM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | pump failure | pedestrian walking in parking lot | unknown | unknow | No |  | 2024-07-26 | 11:00 AM | unknown | 0 |  | property owner called a plumber | Stafford | 88 W Stafford Rd, Stafford, CT

## STAMFORD
Reporting Utility | Status | Incident Type | Weather Conditions |  |  | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAMFORD | Closed | Sewage Bypass | Dry | 8604 |  | 2024-08-22 | 10:15 AM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | Our mechanical bar screens operated under water during the August 18 rainstorm and as a result two of them are down. The one bar screen running cause a surge in our wet well and the high level in the well called for three pumps to come on. The high flow b | Bystander alerted our staff about the spill. | About 1000 gallons. | Estimated by the runoff on the parking lot. | Yes | Stamford Harbor East Branch | 2024-08-22 | 10:15 AM | 1,000 gallons | 1000 |  | The overflow was brief and solve itself, however, to prevent this from happening while we repair our bar screens, we disabled all headworks pump except two. | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Rain greater than 4" per hour | 8563 | Secondary Clarifier #4 is down being painted. During the high flow event the Secondary Distribution Box was overwhelmed until flows came down. Report# 8563. During the | 2024-08-18 | 04:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Greater than 4" rainfall, not around the plant's location but northern part of town, brought very high flows to the headworks exceeding the plant’s peak flow capacity. | Operator doing his round discover the overflow on Secondary Distribution box and the channels feeding it. | The overflow is ongoing and the amount of the overflow is in the thousands of gallons of partially treated raw sewage. The forecast is calling for more rain in the coming hours. It will be impossible to determine the total amount of the overflowl | Overflow is undetermined and ongoing in the thousands of gallons. | Yes | Stamford's Harbor East Branch | 2024-08-18 | 07:30 PM | 150,000 gallons | 150000 |  | Rain intensity subsided | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 8556 | plant reached a max flow of 67MGD. As noted in previous reports primary 1 is undergoing refurbishment. With one Primary Clarifier online the Primary Distribution Box overflowed even with the Bypass gate being triggered. Report#8556. As stated in previous reports | 2024-08-18 | 10:30AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Foreman and operator were right by primary distribution chamber when it happened and were able to minimize | 500 to 800 gallons | Observation | Yes | Stamford Harbor East Branch | 2024-08-18 | 10:30AM | Estimated 1000 gallons | 1000 |  | Opened the bypass gate to allow high flows directly to the aeration tanks. | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 8482 |  | 2024-08-06 | 08:45 PM | Treatment Plant | Raw Sewage | Other | 3rd and 4th Raw Sewage Pump came on. 4th pump was not needed, so i shut it off. I went out to check the Primary Distribution box to ensure the Primary by pass gate opened by the float ball. It did not. Primary Distribution box was overwhelmed. | Saw evidence of of spill around primary distribution box. | 3,000 Gallons estimated. | estimated 3,000 gallons | Yes | Stamford Harbor East Branch. | 2024-08-06 | 08:45 PM |  | 3000 |  | by manually opening the gate. Plant electrician is looking into why the float ball did not open the gate. | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry |  |  | 2024-04-30 | 11:00 AM | Treatment Plant | Raw Sewage | Sewage Line Break, Crack or Failure |  | Water leaked into the contractor's pit upgrading our Primary Clarifier discharge pipe. | 4,000 gallons | Empirically, since there is no flowmeter in place and the leak happened underground. | No |  | 2024-04-30 | 02:00 PM | 4,000 gallons. | 4000 |  | Main gate to the plant was shut down and Headworks influent pumping turned off. Primary Distribution Box lowered and a temporary Test-ball Plug set. A permanent fix will be schedule at a later day. | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Rain 1-2" per hour |  |  | 2024-03-23 | 09:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Heavy precipitation caused a portion of the sanitary sewer line to be surcharged. | City Highway Department reported a dislodged manhole cover to WPCA. | Approximately 20 gallons. | Visual estimate was determined. | Yes | Possibly leaked into Holly Pond. | 2024-03-23 | 09:15 PM | Approximately 20 gallons. | 20 |  | Manhole cover was reinstalled. | Stamford | E Main St, Stamford, CT
[19 empty] | TOTAL VOLUME | 159020

## STONINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
THESE BYPASSES WERE REPORTED DUE TO HIGH FLOW AT THE PLANT BUT DID NOT RESULT IN SOLIDS LEAVING THE PLANT AND ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
STONINGTON - MYSTIC | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-13 | 06:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant check | N/a | n/a | Yes | Mystic River | 01/13/2024 | 03:45 PM | N/A. | 0 | N/A. | Rain Event ended. | Stonington | 22 Edgemont St, Stonington, CT
STONINGTON-BOROUGH WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-06-06 | 08:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Permit required sampling. Visual of sample. | 1.1 MGD | Plant flow meters | Yes | Stonington Borough Harbor | 06/07/2024 | 00:00 AM | N/A. | 0 | N/A. | Rain/Storm event ended | Stonington | 2 High St, Stonington, CT
STONINGTON-BOROUGH WPCF | Closed | Sewage Bypass | Dry | 2024-01-13 | 06:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant check | N/A | Flow trends showed flow at or above permitted flow capacity since approximately 0600. | Yes | Stonington Borough Harbor | 01/13/2024 | 03:45 PM | N/A. | 0 | N/A. | Rain/Storm event ended | Stonington | 2 High St, Stonington, CT
[17 empty] | TOTAL VOLUME | 0

## STRATFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STRATFORD | Closed | Sewage Bypass | Dry | 2024-11-06 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Other | Broken diffuser pipe in aeration basin, loss of tankage volume (1.2MG), taken down to repair it | Visual through final effluent | approximately 3.3 MG | SCADA trending | Yes | Housatonic River | 2024-11-07 | 02:00 AM | 3.3MG | 3300000 |  | corrective action: Mixers off, increase RAS rate, add PAC, tank repaired- began filling | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2024-09-12 | 06:00 AM | Treatment Plant | Sludge Spill | Other | Anoxic tank was off line and sprinkler system being left on resulted in overflow. | During operator rounds | less than 100 gallons | Sprinkler flow rate and time elapsed between rounds. | Yes | Housatonic River | 2024-09-12 | 07:00 AM | Less than 100 gallons | 90 |  | Misters shut off while repairs were in progress. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2024-08-20 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | resident called | 50-100 gallons | visual estimate | No |  | 2024-08-20 | 10:00 AM | 50- 100 gallons | 90 |  | jetted sanitary line | Stratford | Huntington Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-04 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Up to 25 MGD during the event | UV "Low Dose" alarm | Approx. 4.8 MG | SCADA trend chart | Yes | Housatonic River | 2024-04-04 | 07:45 PM | Approx. 4.9 MG | 4900000 |  | Chemical addition (PAC), RAS control, Aeration Control, mixers off. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-23 | 06:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Low UV dose alarm | 20 MGD | SCADA Flow trend | Yes | Housatonic River | 2024-03-24 | 01:30 AM | Approx. 5.8 MG | 5800000 |  | RAS rate control, turn off mixers, chemical addition (PAC), aeration control. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Some solids loss | UV Dose alarm | approx. 1 MG/HR | SCADA flow trend | Yes | Housatonic River | 2024-03-07 | 01:00 PM | 10 MG | 10000000 | SCADA Trend | Flow control (open bypass to anoxic zone), chemical dose (PAC), equipment management mixers off and aeration to a minimum. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 02:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Excessive Flows | Low UV dose alarm | TBD | SCADA Flow Data | Yes | Housatonic River | 2024-01-10 | 05:15 PM | Approx. 13 MG | 13000000 |  | Chemical addition(PAC), RAS flow control, shut off mixers, and minimize aeration | Stratford | 105 Beacon Point Rd, Stratford, CT
[17 empty] | TOTAL VOLUME | 37000180

## TORRINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TORRINGTON WPCF | Closed | Sewage Bypass | Snowmelt | 2024-12-24 | 10:30AM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | most likely small fracture in pressure main | routine inspection | minimal barely noticable | estimated | Yes | still river | 2024-12-26 | 02:30 PM | 10 | 10 |  | Break in pipe was exposed and repaired. | Torrington | 1821 Winsted Rd, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2024-03-21 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | staff working o right of way discovered, raw water discharging out of the ground... | 50 gph | best guess from observation | Yes | Still River | 2024-12-26 | 01:00 PM | 50 gallons | 50 |  | contractor made repair | Torrington | 1780 Winsted Rd, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2024-01-30 | 07:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | blockage in sewer main | manhole that overflowed was in someones back yard. He said he noticed it today so i assume it could not have been overflowing longer than today. also the other neighbors would have seen it if it was going on longer | 500 gallons | estimated to the best of my ability | Yes | No name small stream that goes from Aetna Ave. to Oakbrook Ln | 2024-01-30 | 04:30 AM | estimated to be 500 gallons | 500 |  | cleared blockage with vactor | Torrington | 85 Aetna Ave, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-24 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Street department noticed liquid coming out of manhole cover | 10 gallons | estimated. There was barley anything coming out of manhole when i arrived because its not a high flow line | No |  | 2024-01-24 | 03:00 PM | 10 gallons | 10 |  | cleared blockage with vactor. | Torrington | 538 Litchfield St, Torrington, CT
[17 empty] | TOTAL VOLUME | 570

## TRUMBULL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TRUMBULL | Closed | Sewage Bypass | Dry | 2024-10-11 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor while installing a new sanitary sewer force main on Old Town Road hit the current operating sanitary sewer force main. | Contractor / inspector called in | 300 gal | Truck capacity | No | No Sewage to any water body or storm rain. All sewage was contained with in the trench and was removed via a Vac Truck. | 2024-10-11 | 10:30AM |  | 300 |  | Vac Truck | Trumbull | 1545 Old Town Rd, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2024-08-29 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Air pocket in Force Main. | DPW Supervisor | 5-10 gpm | Visual | No |  | 08/29/2024 | 09:00 AM | Estimated | 300 |  | The flow was diverted to an auxilary force main while a section of the primary force main was repaired | Trumbull | 7 Whitney Ave, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2024-05-13 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Force Main Failure | Police Department Call | 10 gpm | visual | No |  | 05/14/2024 | 05:00 PM | 14400 gal | 14400 | a portion of the station average daily flow 120000 gal/day | The cracked in line was replaced | Trumbull | 75 Merritt Blvd, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2024-05-03 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident called in | 20 gal/ min | Visual inspection | No |  | 05/03/2024 | 10:30 AM | 600 GAL | 600 | ESTIMATED | Flow was diverted to an auxilary force main. The failed section was replaced. | Trumbull | 6466 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2024-03-27 | 06:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | Tree Roots | Resident called | 5 gpm | by visual examination | No |  | 04/27/2024 | 10:30 PM | 1500 | 1500 | OBSEVATION ESTIMATED FLOW | WE WERE ABLE TO RESTORE FLOW AFTER JETTING THE LINE. WE THEN VIDEO THE LINE AN DETRMINED THAT A SETION OF THE LINE NEED TO BE REPLACED A 12- SECTION WAS REPLACE ON 4-1-2024 | Trumbull | 9 Valley View Rd, Trumbull, CT
[17 empty] | TOTAL VOLUME | 17100

## VERNON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
VERNON WPCF | Closed | Sewage Bypass | Dry | 2024-08-28 | 11:45 AM' | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | None | Water leak flowing from lawn into parking lot. CT Water notified Vernon WPC when determined it was not potable water. | 5 gallons/minute | Visual estimate | Yes | Flowing into catch basin which ultimately leads to Hockanum River | 2024-08-28 | 09:00 PM | 975 Gallons | 975 |  | Physical repair of force main by excavation to expose pipe, shut down of pump station, drained the force main and installed band to damaged area. | Vernon | 243 Hartford Turnpike, Vernon, CT
ELLINGTON - CRYSTAL LAKE & HOCKANUM | Closed | Sewage Bypass | Dry | 2024-09-17 | 11:00 AM | Manhole | Raw Sewage | Mechanical Equipment Failure |  | Odor reported & investigated. | Unknown | N/A | Yes | Hockanum River | 2024-09-17 | 03:00 PM | 50 | 50 |  | Unplugged main bypass pump & repaired backup pump. | Vernon | 100 Windsorville Rd, Vernon, CT
[17 empty] | TOTAL VOLUME | 1025

## WATERBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-06 | 07:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | There where sticks found in the manhole that caused the blockage | A passerby contacted Jacobs to investigate. | 30 gallons | visual | No | N/A | 2024-11-06 | 08:30 AM | 30 gallons | 30 |  | Jetter released the blockage and removed sticks from the manhole invert | Waterbury | 48 Lynbrook Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-10-29 | 08:15 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Structural failure of sewer line/manhole | resident emailed Jacobs' maintenance supervisor | 1,000 GPH | Visual estimate | Yes | Trumpet Brook (Waterbury) | 2024-10-29 | 01:00 PM | 5,400 gallons | 5400 |  | Emergency contractor was called in to repair the failed sanitary line. | Waterbury | 535 Bunker Hill Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-10-16 | 02:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | A section of the pipe has disconnected | DPH contacted Jacobs to investigate | 900 gallons per hour | 5 gallon bucket volume estimator | Yes | Steele Brook | 2024-10-16 | 08:15 PM | 5,400 gallons | 5400 |  | Temporary repair was performed on 10/16/24 to stop the bypass (temporary pipe was installed). Permanent repair included installing, anchoring, and concrete encasing the pipe. Final repairs will be completed on 10/21/24. | Waterbury | 1588 Watertown Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-09-03 | 09:45 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | A temporary plug allowed sewage to seep by into an excavation | Jacobs employee was monitoring it. | 150-200 gallons | Visual | No |  | 2024-09-03 | 10:30 PM | 180 gallons | 180 |  | By-Pass plug was reinflated to proper inflation poundage. | Waterbury | 200 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-08-18 | 05:00 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Heavy Rain event | SCADA system alarm | 400 GPM | Pipe diameter calculator flow rate | Yes | Welton brook / Naugatuck river | 2024-08-18 | 09:30 PM | 108,000 gallons | 108000 |  | Rain event ended. Pump station was maintaining without assistance. | Waterbury | 133 Maybrook Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-08-18 | 05:45 PM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | Plant experienced influent flows of 84+MGD so operators opened the gate | Unknown at this time | Unknown at this time | Yes | Naugatuck River | 2024-08-18 | 10:30 PM | Unknown - there is no way to quantify volume from the south chamber | 500000 |  | Rain subsided. Operators maximized capacity of the plant | Waterbury | 210 Municipal Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-07-25 | 02:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | A stick from a private line got lodged and gathered rags to cause the blockage. | Qalert system complaint | 100 gallons | Visual | Yes | Beaver Pond Brook | 2024-07-25 | 04:00 PM | 100 gallons | 100 |  | Jetter truck cleared blockage and removed sticks and rags | Waterbury | 90 Stonefield Dr, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-06-28 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time | a Phone call into Jacobs Water Pollution Control | 2,000 Gallons | Puddle calculator | No |  | 2024-06-28 | 11:15 AM | 2,000 gallons | 2000 |  | Jetter truck was dispatched to clear the blockage. Blockage was cleared and lime was applied to sanitize the area | Waterbury | 1970 Thomaston Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-06-21 | 05:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Collections operator confirmed pipe was compromised | 20 GPM X 60 min. = 1,200 GPH | visual calculating | Yes | Trumpet Brook | 2024-06-24 | 08:30 AM | 67,800 | 67800 |  | A subcontractor was called in to repair the broken pipe. | Waterbury | 105 Trumpet Brook Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-26 | 01:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | When the blockage was released there were sticks, parts of towels, water bottles and rags found. | Waterbury Engineering Dept. discovered it while working in the area. | 3,750 gallons | Sewer manhole overflow calculator. | Yes | Mad river interceptor | 2024-04-26 | 02:30 PM | 3,750 gallons | 3750 |  | A jetter truck was dispatched to investigate and cleared the blockage. Lime was applied to the affected areas. | Waterbury | 168 Berkeley Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-01 | 06:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | During the wet weather event on 3/23/24 (2.7 inches of rain), aeration tank #2 air diffuser broke. In order to perform the repairs, the aeration tank had to be dewatered. The flow from the tank along with high flows from the rain events overwhelmed the lo | Operator doing rounds. | 196,153 gallons | Equation for rectangular weirs | Yes | Naugatuck RIver | 2024-04-01 | 08:15 PM | 196,153 gallons | 196153 |  | Flow directed to lower clarifiers was adjusted. Partially treated effluent was disinfected since the UV system is already put in service in preparation for disinfection season. | Waterbury | 210 Municipal Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:30 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Heavy rain event | Collections Operator received alarm. | 50 GPM | Manhole SSO | Yes | Welton Brook | 2024-01-10 | 03:45 AM | 10,500 gallons | 10500 |  | The Pump Station was maintained with a tanker truck until the flow was able to be maintained by the pump station pumps | Waterbury | 52 Terrell Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 01:00 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Heavy rain event | SCADA system alarm | unknown at this time | visual | Yes | Welton Brook | 2024-01-10 | 03:45 AM | 156,750 gallons | 156750 |  | We maintained the pump station with tanker trucks until the pump station pumps could maintain the flow. | Waterbury | 133 Maybrook Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 01:00 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | In order to protect the plant, the Emergency response plan for plant bypassed was followed and the south chamber gate (84+ MGD) was opened by the operator. | Unknown | There are no means to quantify final volume. | Yes | Naugatuck River | 2024-01-10 | 10:00 AM | Unknown | 150000 |  | Gate was closed once flows decreased to less than 84 MG. | Waterbury | 210 Municipal Rd, Waterbury, CT
[17 empty] | TOTAL VOLUME | 1206063
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY'S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-12-30 | 10:30AM | Lateral - Private | Raw Sewage | Unknown | Private lateral blockage | Field crew noticed while doing CBYD | 25 gallons | Visual | No | N/A | 2025-01-06 | 09:00 AM | Waiting on DPH report |  |  | Waiting on DPH report | Waterbury | 285 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-12-27 | 01:45 PM | Lateral - Private | Raw Sewage | Unknown | Unknown. This is a private lateral issue | Jacobs field crew noticed while doing CBYD markouts | 25-30 gallons | Visual | No | N/A | 2024-12-30 | 11:30 AM | DPH determined 30 gallons |  |  | • Case was assigned to Inspector Manuel on 12/27/2024.• Inspector Manuel spoke with the landlord on sight 12/27/2024 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 12/30/2024, the re-inspection was cond | Waterbury | 73 Tudor St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-12-26 | 11:00 AM | Lateral - Private | Raw Sewage | Unknown | Blockage in a private lateral | Qalert system | 10-20 gallons | Visual | No | N/A | 2024-12-30 | 11:30 AM | Waiting on DPH report |  |  | Waiting on DPH report | Waterbury | 75 High St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-12-02 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 10-15 gallons | Visual | No | N/A | 2024-12-05 | 12:00 PM | DPH reports 75 gallons |  |  | • Case is assigned to Inspector Simoes on 12/02/2024.• On 12/02/2024 a NOV was sent out to the landlord notifying of the violations. • On 12/05/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean a | Waterbury | 46 Coe St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-29 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown blockage | Called by Street Dept foreman | 30 | Visual | No | N/A | 2024-12-02 | 10:00 AM | DPH estimates 50 gallons |  |  | • Case is assigned to Inspector Wood on 11/29/2024.• The inspector got in touch with Property owner on 11/29/2024 and they stated that they would abate sewage discharge.• On 12/02/2024, the re-inspection was conducted and the sewage backup was abate | Waterbury | 46 Cherry St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-20 | 01:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown Blockage | Qalert system | 30 gallons | Visual | No | N/A | 2024-11-22 | 12:00 PM | DPH reports final quantity to be 40 gallons |  |  | • Inspector Simoes got in touch with the landlord on 11/20/24.The landlord stated that he would have the blockage abated. • On 11/22/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized w | Waterbury | 51-55 Ludlow St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-15 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | blockage | Qalert system | 40 gallons | Visual | No |  | 2024-11-19 | 03:15 PM | DPH reports 25 gallons |  |  | • Inspector Eddy got in touch with the landlord on 11/15/24.The landlord stated that he would have the blockage abated. • On 11/19/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized wit | Waterbury | 14 S Reid St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-14 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 10-15 gallons | Visual | No | N/A | 2024-11-15 | 04:00 PM | DPH reports 50 gallons |  |  | • On 11/15/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized | Waterbury | 285 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-13 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | DPH contacted Jacobs to investigate | 10-15 gallons | Visual | No | N/A | 2025-01-14 | 01:00 PM | DPH reports 50 gallons |  |  | Remediation Action: • Case is assigned to Inspector Nelson Simoes on 11/13/2024.• Inspector Simoes got in touch with the landlord on 11/13/2024.The landlord stated that he would have the blockage abated. • On 11/14/2024, the re-inspection was conduc | Waterbury | 113 Robbins St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-11-13 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Called by DPH | 10-15 gallons | visual | No | N/A | 2024-11-14 | 01:00 PM | DPH reports 50 gallons |  |  | • Inspector Simoes got in touch with the landlord on 11/13/2024.The landlord stated that he would have the blockage abated. • On 11/14/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized | Waterbury | 113 Robbins St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-10-31 | 12:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 5-10 gallons | Visual | No | N/A | 2024-11-04 | 11:00 AM | DPH reports 50 gallons |  |  | • Case is assigned to Inspector Tom Watson on 10/31/2024.• Inspector Watson got in touch with the landlord on 10/31/2024.The landlord stated that he would have the blockage abated. • On 11/04/2024, the re-inspection was conducted and the sewage back | Waterbury | 83 Southview St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-07-22 | 04:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time | Qalert system | 50-100 gallons | Visual | No | Mad river interceptor | 2024-07-25 | 07:15 AM | DPH reports 150 gallons. |  |  | • Inspector Eddy got in touch with the landlord on 7/22/24.The landlord stated that he would have the blockage abated. • On 7/25/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized with | Waterbury | 250 Orange St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-07-22 | 09:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 10-20 gallons | visual | No | n/a | 2024-08-12 | 12:00 PM | DPH reports 25 gallons |  |  | • Inspector Wood got in touch with the landlord on 7/22/24.The landlord stated that he snaked from basement • On 8/12/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 174 Wood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-07-15 | 09:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time - private property | Qalert system | 20-30 gallons | Visual from debris on sidewalk and roadway | No | n/a | 2024-07-18 | 03:00 PM | DPH estimates 50 gallons |  |  | • Inspector Watson got in touch with the landlord on 7/16/24.The landlord stated that he called a company to have the blockage abated on 7/18/24. • On 7/18/2024, the re-inspection was conducted and the sewage backup was abated and the affected area wa | Waterbury | 61 Ashley St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-06-20 | 03:00 PM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time | Qalert system | 30-40 gallons | Visual | No | N/A | 2024-06-21 | 03:00 PM | DPH reports 20 gallons |  |  | DPH reports , • On 6/21/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 151 Wall St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-06-06 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time | Qalert system | 10-20 gallons | Visual | No |  | 2024-06-08 | 03:00 PM | DPH estimates 20 gallons |  |  | • Inspector Eddy got in touch with the landlord on 6/6/24.The landlord stated that he called a company to have the blockage abated. • On 6/8/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and san | Waterbury | 15 Camp St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-05-31 | 02:00 AM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Feeney Brothers broke the lateral for 70 Vail St. American Rooter was called to repair the break. the curb box is still discharging. American rooter called back by Jacobs to investigate. | Called from DPH | 20-30 gallons | Visual | No |  | 2024-06-02 | 02:00 PM | DPH estimates 20 gallons |  |  | • Jacobs got in touch with the Router Rooter company and confirmed that the lateral was blocked with baby wipes. The Router Rooter cleared the blockage. The sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 70 Vail St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-05-07 | 00:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | unknown at this time | Qalert call system | 25 GPM | SSO manhole calculator | No |  | 2024-05-08 | 02:30 PM | DPH reports 100 gallons |  |  | • The inspector got in touch with Property management on 5/7/2024 and they stated that they would call a company in to address the outbreak.• On 5/8/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean | Waterbury | 943 Wolcott St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-30 | 08:00 PM | Lateral - Private | Raw Sewage | Other | Cross connection of private lateral discharging into storm system | lateral and potential illicit connection inspections performed as part of the City project at Bank Street. | Uknown at this time | Unknown at this time | Yes |  | 2024-05-01 | 11:00 AM | Unknown - Its unknown when the cross connection started so there is no way to calculate total of gallons bypassed. |  |  | City contractor disconnected the private lateral from the storm system and reconnected it to the sewer line | Waterbury | 123 Bank St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-24 | 10:30AM | Lateral - Private | Raw Sewage | Unknown | Potential compromised private lateral/curb box | Collections Manager was driving around the City and saw the curb box discharging into the street. | 20 gallons | visually | No |  | 2024-04-25 | 12:30 PM | DPH reports 25 gallons |  |  | • The inspector got in touch with the landlord and the blockage was cleared on 04/25/2024. • On 04/25/2024, the re-inspection was conducted and the affected area was clean and sanitized with 10% bleach | Waterbury | 406 Baldwin St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-15 | 12:15 PM | Lateral - Private | Raw Sewage | Unknown | Sewage coming from sidewalk | Citizen call | 20-30 gallons | Visual | No |  | 2024-04-16 | 03:30 PM | DPH reports 50 gallons |  |  | • The inspector got in touch with Property owner on 4/15/2024 and they stated that they would abate sewage discharge from curbbox.• On 4/116/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and san | Waterbury | 80 Charles St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-10 | 07:30 AM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Contacted by DPH | 50-70 gallons | Visual | Yes | Naugatuck river | 2024-04-14 | 03:30 PM | DPH reports 150 gallons |  |  | • On 4/14/2024, the re-inspection was conducted and the sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 203 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-04-10 | 08:00 AM | Lateral - Private | Raw Sewage | Other | Private lateral by-pass | Contacted by DPH | 10-20 gallons | Visual | No |  | 2024-04-10 | 12:45 PM | DPH reports 50 gallons |  |  | • The inspector got in touch with Property owner on 4/9/2024 and they stated that they would call a company and abate sewage discharge | Waterbury | 148 Plaza Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-02-09 | 08:45 AM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time | A passer- by contacted WPCF | 25 GPM | SSO calculator | Yes | Beaver Pond Brook | 2024-02-09 | 12:45 PM | DPH reports 250 gallons |  |  | • The inspector got in touch with McDonalds management on 2/9/2024 and they stated that they already called a company in to address the outbreak . The sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 530 Reidville Dr, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2024-01-02 | 10:15 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown. | Street Dept contacted Jacobs | 400 gallons | Visual | Yes | Sled haul Brook | 2024-01-03 | 12:15 PM | DPH reports 550 gallons |  |  | DPH reported the management company had an outside contractor clear the blockage, cleaned and sanitized with 10% bleach. | Waterbury | 277 Fairfield Ave, Waterbury, CT

## WEST HARTFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-10-17 | 05:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | PLUMBER CALLED IN REPORTING SEWER ISSUE | LESS THAN 50 GAL | MDC PERSONNEL | No |  | 2024-10-17 | 07:15 PM | LESS THAN 100 GAL | 100 |  | M/S WAS FLUSHED WITH JET TRUCK BLOCKAGE WAS RELIEVED | West Hartford | 52 Boulanger Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-10-13 | 08:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | ROOTS AND GREASE | HOME OWNER | < 100 GALLONS | MDC PERSONNEL | No |  | 2024-10-13 | 12:00 PM | < 100 Gallons | 100 |  | Main sewer flushed by jet truck and stoppage relieved | West Hartford | 192 Mountain Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-19 | 09:45 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | High flows due to Rain Event | MDC personnel | > 1 Mg | MDC Personnel | Yes | Piper Brook | 2024-08-21 | 02:00 PM | 1million+ | 1000000 |  | Levels receded. | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-19 | 05:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | No | TROUT BROOK RIVER | 2024-08-19 | 09:45 PM | 75,000 Gallons | 75000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-19 | 05:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | Yes | TROUT BROOK RIVER | 2024-08-20 | 07:00 AM | 4.237 MG | 4237000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 05:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | Yes | TROUT BROOK RIVER | 2024-08-18 | 10:00 PM | 186,000 Gallons | 186000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-08-18 | 05:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | Yes | TROUT BROOK RIVER | 2024-08-19 | 04:45 AM | 3.228 MG | 3228000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-06-30 | 02:45 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | > 100,000 GALLONS | SCADA | Yes | TROUT BROOK | 2024-06-30 | 04:00 PM | 152,000 Gallons | 152000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-18 | 01:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFOW DUE TO WET WEATHER | MDC SCADA SYSTEM | <1000MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2024-04-18 | 06:15 PM | 0.302MG | 302000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-12 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PER OUR SCADA SYSTEM | 1000 GLS | SCADA SYSTEM | Yes | PIPER BROOK | 2024-04-12 | 11:45 PM' | 3.659 MG | 3659000 |  | RAIN EVENT ENDED EXCESSIVE FLOWS RECEDED | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-12 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 1000 GALS | MDC SCADA | Yes | TROUT BROOK | 2024-04-12 | 08:45 AM | 200,000 GAL | 200000 |  | WET WEATHER ENDED EXTRANEOUS FLOWS SUBSIDED | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-03 | 06:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT | MDC SCADA | BETWEEN 100 AND 1,000 GALLONS | MDC SCADA | Yes | PIPER BROOK | 2024-04-06 | 01:30 PM | 20.722MG | 20722000 |  | Overflow was eliminated once elevated sewer flows recede back to normal | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-04-03 | 07:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1,000 GAL | MDC SCADA | Yes | TROUT BROOK | 2024-04-04 | 06:15 PM | 4.316mg | 4316000 |  | Levels receded | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-03-31 | 01:30 PM | Basement | Raw Sewage | Unknown | Soft stoppage | Home owner | <100g | MDC personnel | No |  | 2024-03-31 | 03:00 PM | <100g | 100 |  | MDC jet truck relieved M/S stoppage | West Hartford | 47 Prescott St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-28 | 08:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | SCADA | 1.797MG | SCADA | Yes | PIPER BROOK | 2024-03-30 | 00:15 AM | 1.79 MG | 1790000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 02:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2024-03-25 | 01:15 AM | 11.312MG | 11312000 |  | BYPASS WILL END ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 05:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-03-23 | 09:15 PM | 0.157mg | 157000 |  | Levels receded | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-23 | 04:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | 1000MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-03-24 | 02:30 AM | 3.115 | 3115000 |  | Levels receded | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-09 | 11:45 PM' | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1,000.00 GLS | MDC SCADA | Yes | TROUT BROOK | 2024-03-10 | 07:45 AM | 121,000 | 121000 |  | WEATHER EVENT ENDED EXCESSIVE FLOWS RECEDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-09 | 10:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | 0.001MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-03-11 | 01:15 AM | 7.28mg | 7280000 |  | Levels receded | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1000 GAL | MDC SCADA | Yes | PIPER BROOK | 2024-03-12 | 11:45 PM' | 38.235mg | 38235000 |  | Levels receded | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 09:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1000 GAL | MDC SCADA | Yes | TROUT BROOK | 2024-03-08 | 00:30 AM | 8.443MG | 8443000 |  | LEVELS RECEDED | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 10:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 100 GAL | MDC SCADA | Yes | TROUT BROOK | 2024-03-07 | 09:30 AM | 0.177MG | 177000 |  | Levels receded | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-02 | 09:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO RAIN EVENT | MDC SCADA SYSTEM | 0.003MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-03-02 | 11:00 PM | 0.099 MG | 99000 |  | Bypass is eliminated once flows drop below overflow. | West Hartford | Chelton Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-02 | 08:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS DUE TO RAIN EVENT | MDC SCADA SYSTEM | 1.072 MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2024-03-03 | 05:00 PM | 2.478mg | 2478000 |  | Levels receded | West Hartford | 123 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-28 | 04:15 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <10MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-01-29 | 00:45 AM | 0.862mg | 862000 |  | Levels receded | West Hartford | Chelton Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-26 | 07:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 6.12 MG | MDC SCADA | Yes | PIPER BROOK | 2024-01-30 | 11:30 PM | 11.292mg | 11292000 |  | Levels receded | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 04:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 100 GAL | MDC SCADA | Yes | TROUT BROOK | 2024-01-14 | 01:15 AM | 5.263 MG | 5263000 |  | EXTRANEOUS FLOWS SUBSIDED ONCE RAIN EVENT ENDED | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 05:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1000 GAL | MDC SCADA | Yes | TROUT BROOK | 2024-01-13 | 10:00 AM | 19,000 | 19000 |  | RAIN EVENT ENDED EXTREANEOUS FLOWS SUBSIDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 10:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Passerby | <1000g | MDC personnel | No | Piper Brook | 2024-01-11 | 07:00 AM | 100-1000g | 850 |  | Levels receded | West Hartford | 1 Jacobs Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 00:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Passerby | <100g | MDC personnel | Yes | Trout Brook | 2024-01-11 | 07:00 AM | 100-1000g | 850 |  | Levels receded | West Hartford | 821 Quaker Ln S, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 01:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT | HOMEOWNER | <100G | MDC PERSONNEL | No |  | 2024-01-11 | 07:00 AM | <100g | 100 |  | Levels receded | West Hartford | 8 Overbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-09 | 10:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | BY-PASS DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-01-11 | 04:15 AM | 11.015mg | 11015000 |  | Levels receded | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-09 | 09:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA system | 38.175mg | MDC SCADA system | Yes | PIPER BROOK | 2024-01-16 | 11:00 PM | 38.225mg | 38225000 |  | Levels receded | West Hartford | 123 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-09 | 11:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | BY-PASS DUE TO WET WEATHER EVENT | MDC SCADA SYSTEM | <1000G | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2024-01-10 | 05:00 PM | 1.18mg | 1180000 |  | Levels receded | West Hartford | Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-01-01 | 01:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Home owner | <100g | MDC personnel | Yes | Trout Brook | 2024-01-01 | 07:00 PM | <100g | 100 |  | Cleared with Jet truck | West Hartford | 62 Selden Hill Dr, West Hartford, CT
[17 empty] | TOTAL VOLUME | 179142200

## WEST HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-11-22 | 02:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | grease blockage | property owner | 45 gallons | visual | No |  | 2024-11-22 | 03:00 PM | 45 gallons | 45 |  | property owner | West Haven | 48 New St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-11-15 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Phone call to WPS. | 20 | Visually | No |  | 2024-11-15 | 12:45 PM | 20 gallons | 20 |  | Used Vacall truck to break plug up. | West Haven | 314 Campbell Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-10-11 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | called in by resident | 80 gallons | visual | Yes | cove river | 2024-10-11 | 01:30 PM | 80 gallons | 80 |  | city jetted blockage cleaned up area will bill and fine property owners | West Haven | 23 Treat St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-08-24 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | apartments lateral does not flow well into manhole connection and rags build up | apt.. owners called in | 25 gallons | visual inspection | No |  | 08/24/2024 | 11:45 AM | 25 gallons | 25 | Visual | jetted and vac out blockage | West Haven | 376 W Spring St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-07-18 | 07:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Visually | 150 gallons | Visually | Yes | Cove River | 2024-07-18 | 08:00 PM | 150 gallons | 150 |  | Plug-up was relieved. | West Haven | 403 Saw Mill Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-07-18 | 07:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Visually | 1,000 gallons | Visually | No |  | 2024-07-18 | 08:00 PM | 1,000 gallons | 1000 |  | Blockage was relieved from city line and Service Master was called to clean. | West Haven | 403 Saw Mill Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2024-06-04 | 06:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | rag build up | property owner | 50 gallons | visual | No |  | 2024-06-04 | 06:45 AM | 50 gallons | 50 |  | jetted blockage | West Haven | 10 Industry Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-03-23 | 05:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Dawson Ave. Pump Station could not keep up with excessive flows causing discharge from AMH. | Visually | 2,500-5,000 gallons | Visually | No |  | 2024-03-23 | 10:00 AM | 2,500-5,000 gallons | 4000 |  | Dawson Ave. Pump caught up to flows | West Haven | Ocean Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-03-23 | 05:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Main Pump St. Could not keep up with excessive flows causing discharge from AMH. | Visually | 5,000-10,000 gallons | Visually | Yes | Old Field Creek | 2024-03-23 | 10:00 PM | 5,000-10,000 gallons | 8500 |  | Main Pump St. pumps caught up to flow. | West Haven | Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2024-03-10 | 06:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | 2 pumps failed during rain event | by employee working the station during rain event | 4 million gallons | flow rates and visual inspections | Yes | old field creek | 2024-03-10 | 06:00 PM | 4 million gallons of | 4000000 |  |  | West Haven | 160 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-06 | 11:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | rain event pumps coulnt keep up with excessive flows | alarms from staion | 2k gallons | visual | Yes | L.I sound | 2024-03-07 | 03:15 AM | 2k gallons | 2000 |  | pumps caught up with flow | West Haven | 910 Ocean Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-06 | 11:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | rain event | alarms from station | 5k gallons | visual inspection | Yes | old field creek | 2024-03-07 | 03:00 PM | 5k gallons | 5000 |  | rain even ended pumps caught up with flow | West Haven | 98 Blohm St, West Haven, CT
[17 empty] | TOTAL VOLUME | 4020870

## WESTPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WESTPORT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-11 | 02:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Inflow and infiltration | Resident called it in | 3,000 gallons | Estimated | Yes | Stony Brook/ Nash's Pond | 2024-03-11 | 06:00 PM | 3,000 gallons | 3000 |  | Used septic trucks to suck down the level and located an Illegal sump pump connection to sewer at house #7 Blind Brook Rd and had the homeowner reroute the discharge. | Westport | 4 Blind Brook Rd S, Westport, CT
WESTPORT | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-07 | 08:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Aquarion Called it in. | 100000-200000 Gallons | Estimated | Yes | Muddy Brook | 2024-03-07 | 04:00 PM | 100000-200000 GALLONS | 150000 |  | Put a Clamp on the pipe. | Westport | 9 Hillandale Rd, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2024-01-04 | 02:45 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | outside Contractor broke Sewer Main line. | Contractor | 200-500 gallons | estimated | Yes | Mill Pond | 2024-01-04 | 06:00 PM | 100-200 gallons | 150 |  | Put a Clamp on The Pipe. | Westport | 176 Hillspoint Rd, Westport, CT
[17 empty] | TOTAL VOLUME | 153150

## WETHERSFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-12-18 | 01:15 PM | Manhole | Raw Sewage | Unknown | PAPER TOWELS | MDC PERSONNEL | <100 GALLONS | MDC CREWLEADER | No |  | 2024-12-18 | 02:15 PM | <100 Gallons | 100 |  | MAIN SEWER FLUSHED BY JET TRUCK AND STOPPAGE RELIEVED | Wethersfield | 1870 Berlin Tpke, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-28 | 01:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2024-03-28 | 02:45 PM | < 500 GALLONS | 500 |  | Main sewer flushed by jet truck and stoppage relieved. | Wethersfield | 150 Prospect St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-03-10 | 08:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Rain Event Main Sewer Surcharged | MDC PERSONNEL | <100G | MDC PERSONNEL | Yes | BEAVER BROOK | 2024-08-10 | 23:00 | <100g | 100 |  | Levels receded | Wethersfield | 214 Church St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-03-10 | 08:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT MAIN SEWER SURCHARGED | MDC PERSONNEL | <100G | MDC PERSONNEL | Yes | BEAVER BROOK | 2024-03-11 | 03:00 PM | 100-1000g | 100 |  | Levels receded | Wethersfield | 8 Wells Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2024-03-10 | 09:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT M/S SURCHARGE | PROPERTY OWNER | <100 | MDC PERSONNEL | No |  | 2024-03-11 | 03:00 PM | <100g | 100 |  | Levels receded | Wethersfield | 150 Prospect St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-07 | 04:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | CUSTOMER COMPLAINT TO MDC | LESS THAN 100 GAL | MDC PERSONEL | No |  | 2024-03-07 | 08:00 PM | <100g | 100 |  | Levels receded | Wethersfield | 150 Prospect St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2024-01-11 | 07:00 AM | <100g | 100 |  | Levels receded | Wethersfield | 150 Prospect St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 02:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT | HOMEOWNER | <100G | MDC PERSONNEL | No |  | 2024-01-11 | 07:00 AM | <100g | 100 |  | Levels receded | Wethersfield | 829 Folly Brook Blvd, Wethersfield, CT
[17 empty] | TOTAL VOLUME | 1200

## WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
POQUONOCK WPCF (MDC WINDSOR) | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 02:45 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | High Flow in excess of capacity | Monitoring alarm | 30,000 gallons | weir overflow rate | Yes | Farmington River | 2024-01-10 | 03:15 AM | 30,000 gallons | 30000 |  | Facility Flows returning to manageable levels | Windsor | 1222 Poquonock Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-11 | 05:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Homeowner | less than 100 galons | MDC personnel | No |  | 2024-03-12 | 05:00 PM | <100g | 100 |  | Levels receded | Windsor | 26 Hope Cir, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-10 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2024-03-11 | 08:00 AM | < 100 GALLONS | 100 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal. | Windsor | 54 Green Manor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G |  | No |  | 2024-03-07 | 11:30 PM | <100g | 100 |  | Levels receded | Windsor | 55 Green Manor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-03-07 | 02:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC personnel | No |  | 2024-03-07 | 11:30 PM | <100g | 100 |  | Levels receded | Windsor | 12 London Rd, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-03-06 | 05:45 PM | Basement | Raw Sewage | Unknown |  | CUSTOMER CALLED MDC REPORTING WATER IN BASEMENT | LESS THAN 100 GAL | MDC PERSONEL | No |  | 2024-03-06 | 09:15 PM | LESS THAN 100 GAL | 100 |  | MDC CREWS JETTED MAIN SEWER | Windsor | 79 Poquonock Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2024-01-13 | 01:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PLUMBER | <1000MG | VISUAL OBSERVATION MDC PERSONNEL | No |  | 2024-01-14 | 12:15 PM | < 1000 GALLONS | 1000 |  | Bypass is eliminated once flows dropped. | Windsor | 511 Windsor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 01:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2024-01-11 | 07:00 AM | <100g | 100 |  | Levels receded | Windsor | 110 Rood Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 08:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | Yes | Deckers Brook | 2024-01-11 | 07:00 AM | 100-1000g | 850 |  | Levels receded | Windsor | Arrowbrook Rd, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2024-01-10 | 08:45 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | resident reported. | <100g | MDC personnel. | No |  | 2024-01-11 | 07:00 AM | <100g | 100 |  | Levels receded | Windsor | 25 Clover St, Windsor, CT
[17 empty] | TOTAL VOLUME | 32550

## WINSTED
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WINSTED WPCF | Closed | Sewage Bypass | Dry | 2024-01-11 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility |  | Resident call in | 10000 gal | Visual, flowing at approx 50gal/min | No |  | 2024-01-11 | 10:30AM | 10000 gal | 10000 |  |  | Winsted | 165 W Lake St, Winsted, CT
[17 empty] | TOTAL VOLUME | 10000